Metropolitan King County Council

#### Regional Water Quality Committee

Staff Report

| Agenda Item No.: | 8 |  | Name: | Beth Mountsier |
| --- | --- | --- | --- | --- |
| Briefing No.: | 2014-B0149 |  | Date: | September 3, 2014 |
| Attending: | Steve Tolzman, Water Quality Planner/Project Manager, Wastewater Treatment Division (WTD) |

SUBJECT

A briefing on the preliminary Regional Needs Assessment for the Wastewater Conveyance System.

SUMMARY

The purpose of a Regional Needs Assessment (RNA) is to assess the capacity of the separated portion of the regional wastewater conveyance system and identify where the system will not meet the adopted 20-year peak flow standard through 2060. WTD staff utilize the results of the RNA to update its conveyance system improvement (CSI) program including the conceptual projects and cost estimates for increasing capacity.

The most recent RNA completed in 2005 updated and identified on-going and new capacity issues (as identified in the technical analysis that lead to the 1999 Regional Wastewater Services Plan and the accompanying Operational Master Plan)  in the conveyance system..

Flow monitoring and modeling data and assumptions specifically developed for the I/I Control Program were used to project CSI project needs to allow for an accurate comparison of benefits and costs between CSI projects and I/I reduction projects. As a result, the complete list of CSI projects recommended in 2007 in the CSI Update differed from what was included in the Regional Wastewater Services Plan (RWSP), as updated in 2004.

The major difference is that CSI capacity issues identified in the 2005 RNA were projected through 2050 rather than 2030 - the planning horizon for the RWSP. Additionally, the comprehensive flow metering and modeling data that was used differed from that used during the update of the RWSP. This resulted in some modification of CSI projects expected to be needed by 2030.

Since then, WTD staff have completed the decennial flow monitoring project collecting flow data in the separated portion of the regional wastewater system from 2009 to 2011, and the Puget Sound Regional Council (PSRC) released an updated population and employment forecast in 2013.  The updated RNA uses wastewater flow monitoring data from 2009-2011 and the 2013 PSRC population and employment forecast. WTD staff further refined the PSRC population and employment projections to regional wastewater service area boundaries.  The flow monitoring data, the population and employment forecast, and WTD’s flow forecasting assumptions have been applied to produce an initial list of portion of the separated conveyance system that do appear to not meet the  adopted 20-year peak flow standard.

At this time King County staff are just starting to meet with city and sewer district staff to confirm or update the flow forecasts and population and employment projections – to reflect locally known information about zoning/planning changes that WTD staff may not be aware of, as well as timing of new development in cities.

WTD staff will brief the committee on the process to develop the initial RNA results and the next steps.   At this time there is no ‘report’ for the 2014 RNA – but attached is initial results summary information (Attachment 1) and the PSRC Population and Employment Forecast Summary, August 2014 (Attachment 2) shared with the Metropolitan Water Pollution Abatement Advisory Committee – Engineering and Planning Subcommittee.

BACKGROUND

Regional Wastewater System

King County’s regional wastewater system serves approximately 1.4 million residents within a 420-square-mile service area encompassing portions of King, Snohomish, and Pierce Counties.

It is a large, integrated wastewater collection, conveyance, and treatment system operated by the King County and thirty-four cities and sewer agencies. These cities and sewer agencies (collectively known as local agencies) provide direct sewer collection service to residences and businesses. King County owns and operates regional facilities necessary for wastewater treatment including treatment plants, major conveyance pipes, regulators, and pump stations.

Local Agencies own and operate the facilities necessary for collecting wastewater from

residences and businesses. Their facilities include collector sewers, laterals, side sewers, and some pump stations.

The system of pipes that collects and conveys wastewater was constructed over many decades.  Older pipes, located in most parts of Seattle, are a combined sewer system that collects a combination of stormwater and sanitary sewage. The rest of the region, including some portions of north Seattle, is served by a separated sewer system.

Separated systems have separate collection and conveyance pipes for wastewater and storm water. Separated wastewater systems dedicate their capacity to convey and treat wastewater. Stormwater is not supposed to enter the separated wastewater system.

The following is a summary of King County wastewater system components defined and then tallied for perspective on the current facilities that King County maintains and operates relative to the conveyance system:

- Treatment Plants provide primary and secondary treatment of wastewater before discharging the treat effluent to Puget Sound.

- Conveyance Pipes carry wastewater to the treatment plants.

- Pump Stations house pumps and other equipment that lift wastewater in pipes to higher elevations so that they can continue to flow by gravity.

- Regulator Stations control the flow of wastewater from two or more input pipes to the collection system.

- Combined Sewer Overflow (CSO) or Wet Weather Treatment Plants operate during periods of peak flow following large storm events. They provide primary treatment and disinfection to wastewater diluted by stormwater prior to discharge to Puget Sound.

- CSO Control Structures store excess wastewater diluted by stormwater to prevent overflows into surface waters.

The components that make up the King County regional wastewater system are:

- 5 secondary treatment facilities (including the Vashon and Carnation Treatment Plants and Brightwater which utilizes an MBR technology for secondary treatment)

- 335 miles of regional conveyance pipes

- 42 pump stations

- 19 regulator stations

- 2 combined sewer overflow (CSO) treatment plants

- 38 permitted CSO locations.

- 5,100 miles of collection pipes and numerous pump and regulator stations (owned by the local agencies)

Conveyance Capacity Demand

The two primary factors that drive the need to expand capacity in the ‘separated’ conveyance system are regional population growth, and I/I flows within the system.

Growth in sanitary sewerage from residences and businesses, or “base flow,” volume over time is driven by changes in population and employment in the service area, septic conversions to sewers, and changes in water use levels through conservation efforts.

Based on these factors, base flow in the regional service area was projected in 2005 to grow from approximately 75-million gallons-per-day (MGD) to over 120 MGD by 2050.

The figure (Figure 1) below illustrates the projected growth rate in base flow for the region in 2005. Note that the projected growth in base flow through 2010 was expected to be relatively flat. This is due to the expected immediate positive influence of water conservation efforts that are currently (and still) under way. Projected growth after 2010 assumed that the effects of water conservation will remain constant.

Of the growth factors described above, growth in residential sewered population (from either new development or septic conversions) has the biggest effect on growth in base flow.

Figure 1.  Projected Growth in Base Flow (2005)

I/I is clean stormwater runoff and ground water that enters wastewater collection pipes during periods of rain. Most inflow comes from stormwater; most infiltration comes from groundwater.  I/I significantly affects the capacity of the region’s wastewater conveyance and treatment system because it is the largest contributor to wastewater volumes that must be conveyed and treated in the wet season. About 75-percent of the region’s peak flows in the separated conveyance system comes from I/I1.

Figure 2 is a hydrograph from 2005 that shows how I/I affects regional wastewater volumes that must be conveyed and treated.  As shown, flow volumes can quadruple during rain events when the conveyance system must handle base flow plus I/I (the blue line in Figure 2).

Figure 2.  Impact of Wet Weather – I/I on Wastewater Flows (2005)

In 2005, sixty-three CSI project were identified to the meet the region’s projected capacity needs through 2050.  The projects identified were based on the data gathering and modeling efforts completed for the I/I Control Program and the RNA.  These projects and their estimated costs were used as the basis for conducting benefit/cost analyses or potential I/I reduction projects.  The list of projects and schedule were refined further by the County and local agencies who worked together to develop and recommend a regional I/I control program.  The Regional Water Quality Committee was briefed earlier this year on the preliminary findings of one of those I/I Control projects.

ATTACHMENTS

- Conveyance System Improvement Program Update - Initial Regional Needs Assessment Results for Discussion with Local Agencies, dated September, 2014

The same is true in the combined portion of the system in Seattle – however, there the system is designed to take inflow of stormwater.

The recently completed 2013 Regional Wastewater Services Plan – Comprehensive Review has determined that the average base flow has declined enough that projections for the timing of South Treatment Plant have delayed beyond 2030.