Review of the Lakehaven Utility District’s Water System Plan Update (the Plan)

Service Area The Lakehaven Utility District owns and operates a water system located in the southwest corner of King County adjacent to the Pierce County boundary. Puget Sound and the Green River Valley border the District on the west and east, respectively. The District's northern border generally follows South 280th Street, except for a narrow strip of land extending north along the Puget Sound to South 252nd Street. General government services and land use planning in the District’s water service area are controlled by, and under the jurisdiction of King County, and the Cities of Federal Way, Des Moines, Algona, Auburn, Pacific, Edgewood, and Milton. The City of Kent also provides general government services and land use planning inside the District’s corporate boundaries, but outside of the District’s retail water service area. The District boundary encompasses an area of approximately 34 square miles and provides water service to a residential population of approximately 112,800 through approximately 29,490 connections. Residential water sales account for about 80 percent of the total sales. Commercial, irrigation and public uses account for the remaining sales. The District measures water use with Equivalent Residential Units (ERUs). In 2011, the District served approximately 44,299 ERUs. From 2006 to 2011, the average ERU water use was 215 gallons per day (gpd). The District’s water system includes approximately 450 miles of mainline, 25 production wells, 12 storage tanks, 3 booster pump stations, and 3 flow control facilities connecting the water system to the Second Supply Project pipeline. The Second Supply Project is a joint effort of several South King County utilities and the City of Tacoma to develop additional water supply from the Green River. The average daily demand for water during the years 2008 through 2011 was 9.87 million gallons per day (mgd). Average annual production and purchases decreased from 11.09 mgd in 2006 to 9.13 mgd in 2011. Maximum day demands (MDD) ranged from 15.20 mgd to 22.40 mgd over this period. The District’s peaking factor is 1.95. The District’s non-revenue water ranged from approximately 5 percent to approximately 9 percent, with an average of 7 percent from 2006 to 2011. Reclaimed Water The District does not reclaim water now, but is looking at opportunities for use of reclaimed water including surface irrigation, groundwater recharge by surface percolation, stream flow augmentation through wetlands, direct aquifer recharge, and industrial or institutional reuse opportunities. The District operates its own treatment plants for wastewater management, is not in the wastewater service area of the regional system and consequently did not complete the King County’s Water Reclamation Evaluation Checklist. SEPA The District completed a State Environmental Policy Act (SEPA) checklist for the Plan and, as lead agency under SEPA, issued a determination of nonsignificance for the approval of the Plan on September 25, 2014. There were no appeals.

|  | A. General, water and sewer plan specific King County Code (KCC) 13.24.010 | Comments/findings |
| --- | --- | --- |
| (1) | The code is applicable to water and or sewer utilities that obtain water in unincorporated areas, provide service in unincorporated areas of King County, and/or are component agencies of the regional wastewater system. | The District distributes water in unincorporated areas of King County, making review under KCC 13.24 appropriate. |
| (2) | Water system plans should be submitted every six years or sooner if required by the Washington State Department of Health. | The District’s last water plan was in 2008. The District will seek plan approval from the Washington State Department of Health. |
| (3) | The infrastructure for existing and future service areas based on adopted land use map. | Yes, King County land use and zoning maps were appropriately used in determining the water demand projections. |
| (4) | The Plan contains sufficient information to demonstrate the ability to provide services consistent with the requirements of all applicable statutes, codes, rules, and regulations. | Yes, the Plan demonstrates that the District has ample water supply to provide service consistent with the requirements of all applicable statutes, codes, rules, and regulations. |
| (5) | The Plan is consistent with Washington Administrative Code (WAC) 246-290-100 for the water service. | Yes, the Plan is consistent with the applicable rules. |
|  | B. Consistency requirements: 13.24.060 |  |
| (6) | King County Code related to the installation of fire hydrants and water mains. | Yes, the Plan proposes to provide adequate fire flow; there are several proposed capital improvement projects to increase fire flow for portions of unincorporated King County served by the District. |
| (7) | State and local health requirements. | The Plan has not yet been approved by the Washington State Department of Health. The UTRC review process included a representative of Public Health-Seattle and King County. |
| (8) | Elimination or prevention of duplicate facilities. | The District has written agreements with other water providers regarding areas to be served in order to avoid overlapping jurisdiction and to ensure efficiency in the use of existing facilities. |
| (9) | Promotion of most healthful and reliable services to the public. | Yes. |
| (10) | Provision of service at a reasonable cost, and maximization of use of public facilities. | Currently, the District charges a rate that is in the affordable range. |
|  | C. King County Comprehensive Plan (KCCP) – consistency with provisions and specific policies |  |
| (11) | Consistency with the KCCP and applicable County plans and policies including the Flood Hazard Management Plan and Emergency Response Plan. | Yes, the Plan is consistent with the applicable comprehensive plans. |
| (12) | Consistency with the Coordinated Water System Plans adopted in KCC 13.28. | Yes, the Plan is consistent with the South King County Coordinated Water System Plan (CWSP). The District CWSP designated service area boundary is concurrent with its retail service area. |
| (13) | Basin-wide or multi-basin water plans, sewerage plans, or both when approved by the Washington State Department of Ecology or the Washington State Department of Health. | Not applicable. |
| (14) | Applicable state water quality, water conservation (e.g., chapter 90.54 RCW and RCW 90.48.495), and waste management standards. | Yes. The District implements a water conservation program. |
| (15) | Growth Management Act; chapter 36.70A RCW. | Yes, the Plan is consistent with the Growth Management Act. See specific policies below. |
| (16) | Groundwater Management Plans. | The District coordinates wellhead protection management strategies with the municipalities within which wellhead protection areas are located. |
| (17) | Federally-approved habitat conservation plans and recovery plans under Endangered Species Act, and other plans, including regional water supply or water resource management plans. | The District is aware of, and supports, the planning done for salmon recovery purposes. There is no active applicable regional water supply plan. |
| (18) | Applicable requirements to evaluate opportunities for the use of reclaimed water under chapter 90.46 RCW. | Yes, the District evaluated reclaimed water use opportunities. The District is not connected to the regional wastewater system and owns its own wastewater treatment plants. Expansion and modifications to the Lakota Waste Water Treatment Plant, a new membrane polishing facility, and an additional ultraviolet system are planned to produce reclaimed water suitable for groundwater infiltration at the Panther Lake site. Additional treatment processes assumed include nitrogen removal, filtration, and disinfection. The District did not complete the King County Water Reclamation Evaluation Checklist because they are not part of the regional system. |
| (19) | State Environmental Policy Act documentation. | The District completed a SEPA checklist and issued a determination of nonsignificance for approval of the plan on September 25, 2014, with no appeals. |
|  | COUNTYWIDE PLANNING POLICIES |  |
| (20) | DP‐13: All jurisdictions shall plan to accommodate housing and employment targets. This includes: “Coordinating water, sewer, transportation and other infrastructure plans and investments among agencies, including special purpose districts;…”. | Yes, the District does this. |
| (21) | PF‐4: Develop plans for long‐term water provision to support growth and to address the potential impacts of climate change on regional water resources. | The District has a reasonable plan for long-term water supply to meet projected growth. The Plan does not discuss climate change impacts on water supply. The District is self-supplied and a member with others in Tacoma’s Second Supply Project. |
| (22) | PF‐5: Support efforts to ensure that all consumers have access to a safe, reliably maintained, and sustainable drinking water source that meets present and future needs. | Yes, the District does this. |
| (23) | PF‐6: Coordinate water supply among local jurisdictions, tribal governments, and water purveyors to provide reliable and cost‐effective sources of water for all users, including residents, businesses, fire districts, and aquatic species. | The District has agreements in place with neighboring utilities for wholesale water exchanges and emergency supply. |
| (24) | PF‐7: Plan and locate water systems in the Rural Area that are appropriate for rural uses and densities and do not increase the development potential of the Rural Area. | Not applicable as the District does not serve the Rural Area. |
| (25) | PF‐8: Recognize and support agreements with water purveyors in adjacent cities and counties to promote effective conveyance of water supplies and to secure adequate supplies for emergencies. | The District has agreements with neighboring utilities for service area and to assist in emergency situations. |
| (26) | PF‐9: Implement water conservation and efficiency efforts to protect natural resources, reduce environmental impacts, and support a sustainable long‐term water supply to serve the growing population. | From 2006 to 2011, the average ERU water use was 215 gallons per day (gpd). For future demand projections, the 226 gpd/ERU was used to develop a long range in water use projections. The District’s three-year average distribution system loss is 4.3 percent. |
| (27) | PF‐10: Encourage water reuse and reclamation, especially for high‐volume non‐potable water users such as parks, schools, and golf courses. | See 18. The District completed King County’s Water Reclamation Evaluation Checklist. There are no opportunities to use reclaimed water at this time. |
|  | KING COUNTY COMPREHENSIVE PLAN (KCCP) POLICIES |  |
| (28) | F-107: Plan for provision of services to rural areas. | Not applicable. |
| (29) | F-108: King County to work with cities and service providers to establish priority areas for public funding of capital facilities. | The capital improvement program (CIP) is adequate and appropriately focused with funding sources identified. |
| (30) | F-201: All facilities and services should be provided in compliance with provisions and requirements of the Endangered Species Act (ESA) and the Clean Water Act. | Yes, to the extent known, facilities and service are provided consistent with the federal laws. |
| (31) | F-209: Support rural levels of development and not facilitate urbanization. | Not applicable. |
| (32) | F-210: Capital facility plans and improvement programs for services to unincorporated King County are consistent with the KCCP. | Yes, the CIP is consistent with the KCCP. |
| (33) | F-211: King County helps coordinate development of utility facilities. | Yes, to the extent applicable, King County will do this. |
| (34) | F-221: King County shall initiate a sub-area planning process with any service provider that declares, in its capital facilities plan, an inability to meet service needs within service area. | Not applicable. The District did not identify any inability to meet service needs within its service area. |
| (35) | F-223: If a service deficiency is identified in a service provider's existing service area, King County and the applicable service provider shall remedy the deficiency through a joint planning process addressing capital improvement programs and long-term funding strategies reuse programs. | Not applicable. The District did not identify any inability to meet service needs within its service area. |
| (36) | F-231: King County supports coordination of regional water supply planning, sales of excess water supplies among municipalities in the region, water quality programs and water conservation, reuse and reclaimed water programs. | Yes, the District supports regional water supply coordination and has partnered with the City of Tacoma, the Covington Water District, and the City of Kent on the Second Supply Project. |
| (37) | F-232: Water utilities that obtain water from, or distribute water in unincorporated King County, and water utilities formed as special purpose districts under Title 57 RCW are required to submit water system plans to the County for review and approval and shall describe in their plans how they intend to meet their duty to provide service within their retail service areas. | The District is a special purpose district under Title 57 RCW. The District also obtains and distributes water in unincorporated King County, so the plan is subject to review and approval by the King County Council. |
| (38) | F-248 King County shall partner with utilities to publicize water conservation and encourage best management practices that conserve potable water supply through measures that include use of alternative supplies such as reclaimed water. | Yes, the County will do this. |
| (39) | F-246: King County supports interties that allow the transfer of water resources among water utilities to meet the projected demands for growth where such interties meet the requirements of RCW 90.03.383 and are also consistent with any applicable locally adopted comprehensive plans, regional water supply plans, adopted groundwater management plans, watershed plans, approved Coordinated Water System Plans, and response requirements of ESA and Clean Water Act. | The District has interties with other utilities. |
| (40) | F-249: Utilities with more than one thousand service connections required to submit water system plans for approval to King County shall include an evaluation of reclaimed water use opportunities by completing King County’s Water Reclamation Evaluation. | The District did an evaluation of reclaimed water use but did not complete King County’s Water Reclamation Evaluation Checklist because it is not part of the regional system. The District operates its own wastewater treatment plants and is not within the service area of the regional wastewater system. |
| (41) | F-251: In its review of water system plans, the UTRC shall consider the criteria provided in KCC 13.24.010, 13.24.060, and 13.24.070, and determine the plan’s consistency with the following: a. Applicable provisions of the King County Comprehensive Plan, land use plans, and development regulations adopted under the Growth Management Act; b. Approved or adopted regional water resource plans, such as basin plans, groundwater plans, watershed-based conservation and recovery plans developed under ESA, salmon recovery plans developed under chapter 77.85 RCW, water resource plans developed under chapter 90.54 RCW, watershed plans developed under chapter 90.82 RCW, and a regional water supply plan or water resource management plan; c. The County’s Regional Wastewater Services Plan; and d. Other applicable provisions of countywide plans managed by King County, as specified in UTRC Guidance or checklists. | The UTRC did consider these issues and recommends approval of the Plan. |
| (42) | F-252: In reviewing proposals for modified and expanded service area boundaries for municipal water suppliers, the UTRC shall consider, in addition to Policy F-251: a. Compliance by the water system with its water system comprehensive plan, including water conservation elements; b. Whether it can meet its duty to provide service within its service area, as required under chapter 43.20 RCW; and c. Consistency with the service provisions of any applicable Coordinated Water System Plan, as adopted in King County Code Chapter 13.28. | The District is not planning to change its service area. |
| (43) | F-253: Consistent with Countywide Planning Policies, public drinking water system surface water reservoirs and their watersheds should be managed primarily for the protection of drinking water, but should allow for multiple uses, including recreation, when such uses do not jeopardize drinking water quality standards. Public watersheds must be managed to protect downstream fish and agriculture resources. | Not applicable. |
| (44) | F-254: Groundwater-based public water supplies should be protected by preventing land uses that may adversely affect groundwater quality or quantity to the extent that the supply might be jeopardized. The County shall protect the quality and quantity of groundwater used as water supplies through implementation of Policies E-493 through E-497 where applicable. | The Wellhead Protection Program of the District has been incorporated into the County’s critical area ordinances for well capture zones that overlap unincorporated areas. |