SKYWAY INFILTRATION AND INFLOW

REDUCTION DEMONSTRATION

PROJECT EVALUATION REPORT

March 2014

Department of Natural Resources and Parks

Wastewater Treatment Division

SKYWAY INFILTRATION AND INFLOW REDUCTION DEMONSTRATION PROJECT EVALUATION REPORT

MARCH 2014

Prepared for:

201 South Jackson Street

Seattle, WA 98104 http://dnr.metrokc.gov/wtd

Prepared by:

Project #3630037

Skyway Initial Infiltration and Inflow Reduction Demonstration Project Evaluation Report

TABLE OF CONTENTS

Title   Page No.

Chapter 1. Project Overview	1

1.1 Project History	1

1.2 Project Description	3

1.2.1 Project Scope	3

1.2.2 Predicted I/I Reduction	3

1.2.3 Cost-Effectiveness	4

1.2.4 Identified Risks	4

Chapter 2. Final Design, Bidding and Construction	6

2.1 Final Design	6

2.2 Bid Results	6

2.3 Construction Highlights	7

2.3.1 Variations from Final Design	7

2.3.2 Construction Challenges	8

2.4 Final Costs	10

2.5 Warranty Inspection	10

Chapter 3. Project Effectiveness Evaluation	12

3.1 Basin Delineation and Monitoring	12

3.1.1 Basin Boundaries and Flow Meter Locations	12

3.1.2 Basin Boundary Issues	13

3.2 Modeling	14

3.3 I/I Reduction Effectiveness Results	15

3.3.1 Flow Reduction by Basin	15

3.3.2 I/I During a Selected Storm Event	15

3.4 I/I Reduction Effectiveness Summary	16

3.4.1 Effect of Sump Pumps and Foundation Drains	17

3.4.2 Groundwater at Sewers Downslope of Improved Area	17

3.4.3 Incompletely Rehabilitated Properties	17

3.4.4 Diminished Effectiveness Downstream From Project	18

3.4.5 Impact on Need for Other Capital Projects	21

Chapter 4. Lessons Learned	22

4.1 Design	22

4.1.1 Identifying Problem Areas	22

4.1.2 Basin Characterization	22

4.1.3 Design Certainty and Priority of Project Expenditures	22

4.1.4 Consideration of Sump Pumps	23

4.2 Construction	23

4.2.1 Flexibility	23

4.2.2 Performance-Based Scheduling	23

4.2.3 Groundwater Issues	23

4.2.4 Contingency Bid items	24

i

TABLE OF CONTENTS

4.2.5 Side Sewer Replacement ....................................................................................................... 24

4.2.6 Foundation Drains ................................................................................................................. 24

Appendix—Skyway Infiltration and Inflow Reduction Pilot Project and Demonstration Project Methodology and Results

LIST OF TABLES

# No. 	Title 	Page No.

Table 1-1. Medium- and High-Rated Risk Elements and Mitigation Measures ........................................... 5

Table 2-1. Bid Results ................................................................................................................................... 6 Table 2-2. Schedule a Side Sewer and Lateral Variations ............................................................................ 8

Table 2-3. Schedule B Sewer Main and Manhole Variations ....................................................................... 8

Table 3-1. Removal Effectiveness Based on Post-Project Flow Monitoring .............................................. 15

LIST OF FIGURES

No. 	Title 	Page No.

Figure 1-1. Initial I/I Reduction Project Candidate Basins and Related CSI Projects .................................. 2 Figure 1-2. Skyway I/I Reduction Demonstration Project Location ............................................................. 3

Figure 2-1. Pavement Settlement Along Sewer Main Alignment Following Construction .......................... 9

Figure 2-2. Groundwater Following Burst Sewer Main Trench Breaks Out of Pavement ........................... 9 Figure 2-3. Retrofit Trench Drain Captures Groundwater Flow and Alleviates Pavement Settlement ...... 10

Figure 3-1. BLS002 Demonstration Project Basin Boundary with Meter Locations ................................. 13

Figure 3-2. Connected Basin 148F ............................................................................................................. 14

Figure 3-3. Flow by Basin Area for Post-Rehabilitation Storm Event in January 2013 ............................. 16

Figure 3-4. Side Sewer Replacement Status ............................................................................................... 18

Figure 3-5. Full Side Sewer Rehabilitation as Designed ............................................................................ 19

Figure 3-6. Partial Side Sewer Rehabilitation as Constructed .................................................................... 20

ii

# CHAPTER 1. PROJECT OVERVIEW

In 2012, King County’s Wastewater Treatment Division and the Skyway Water and Sewer District (WSD) repaired and replaced sewer mains, side sewers, laterals and manholes in a residential sewer service basin near the southwest end of Lake Washington (Skyway Basin BLS002). The goal of this demonstration project was to reduce infiltration and inflow (I/I) to the sewer system, increasing the unused capacity of the wastewater conveyance system and eliminating the need for a planned wastewater storage facility downstream.

This report summarizes the history of the project, the work performed, follow-up investigations, and findings about the project’s effectiveness in reducing I/I. It describes lessons learned from the project that can be applied to similar work in the future and outlines additional steps needed in order to use the project results for future decision-making.

## 1.1 PROJECT HISTORY

Reducing I/I, which consists of stormwater and groundwater entering a sanitary sewer system from various sources, makes more capacity available for sewage in King County’s wastewater system. This increased capacity helps to prevent overflows and reduces the need for capital projects to expand system capacity. The Skyway I/I Reduction Demonstration Project was an early test of the effectiveness of I/I reduction measures over a large area. The following County programs and projects provided the foundation for developing and implementing the project:

- Regional Infiltration/Inflow Control Program—The King County Regional I/I Control Program was created in 1999 to reduce I/I in the County’s wastewater conveyance system when it is cost-effective to do so. Under this program, the County implemented multiple pilot projects in 2003 and 2004 to test various I/I reduction methods and technologies. For these projects, the County performed sewer system evaluation surveys that included cleaning, CCTV inspection and smoke testing for sources of inflow. Sewer system evaluation survey results were used to design I/I reduction pilot projects that included pre- and postconstruction flow monitoring to determine the projects’ effectiveness. Results of the pilot projects were used to establish assumptions for estimating costs for subsequent I/I reduction projects and the expected amount of I/I reduction. One of the pilot projects, the Skyway Pilot Project, was in a portion of Skyway Basin BLS002.

- Draft Standards, Guidelines, Procedures and Policies—King County and local sewer agencies developed a draft set of design and inspection standards to be used on future projects to reduce and control I/I, based on engineering judgments of best practices. The standards, guidelines, procedures and policies were applied and tested in the Skyway I/I Demonstration Project.

- Executive’s Recommended Regional Infiltration and Inflow Control Program—The six-year I/I program development process culminated in consensus recommendations by the County and local agencies about the future direction of the County’s I/I program. The consensus drew from findings of the flow monitoring, modeling and pilot projects and a benefit-cost analysis, all conducted during the I/I control study. A key recommendation was for the County to implement and evaluate two or three “initial” I/I reduction projects to test the cost-effectiveness of I/I reduction on a larger scale than the pilot projects.

Skyway Initial Infiltration and Inflow Reduction Demonstration Project Evaluation Report

- Conveyance System Improvement Program—King County’s Conveyance System Improvement (CSI) Program outlines needed capital improvements to provide adequate capacity in the County-owned regional wastewater conveyance system. Among the CSI program’s current recommendations is the 0.27-million-gallon Bryn Mawr Storage Facility, which would help to accommodate high system flows downstream of Skyway Basin BLS002.

- King County Initial I/I Reduction Project Predesign Report—Preliminary design recommendations were published in March 2010 for King County’s Initial I/I Reduction Demonstration Projects. The report documents preliminary design evaluations and findings, provides estimates of project cost and benefit, and presents considerations for implementing I/I reduction projects in three basins (see Figure 1-1): Bellevue Basin BEL031, Issaquah Basin ISS003, and Skyway Basin BLS002. Following completion of the Initial I/I Reduction Project Predesign Report, only the Skyway basin project was moved forward to final design and implementation due to budget constraints.

Figure 1-1. Initial I/I Reduction Project Candidate Basins and Related CSI Projects

PROJECT OVERVIEW

## 1.2 PROJECT DESCRIPTION

### 1.2.1 Project Scope

The Skyway Initial I/I Reduction Project, hereafter called the Demonstration Project, aimed to rehabilitate side sewers and laterals serving 343 of the 375 properties in Basin BLS002 using pipe bursting with 4-inch-diameter HDPE pipe. See Section 2.1 Final Design. Figure 1-2 shows an overview of the project area. As an additional project component, the Skyway WSD financed replacement of approximately 20,000 feet of primarily 8-inch diameter sewer mains by pipe bursting and replacement of 90 manholes.

Figure 1-2. Skyway I/I Reduction Demonstration Project Location

### 1.2.2 Predicted I/I Reduction

The Demonstration Project was similar in many ways to the earlier pilot project in this basin, the location of which is also shown on Figure 1-2. Similarities include the age of the sewer pipe, the materials used for rehabilitation, neighborhood characteristics, and the condition of the sewers. The 2003/2004 Skyway Pilot project resulted in an 88.5-percent reduction in peak I/I. However, the County and local sewer agencies established a more conservative reduction target range of 60 to 75 percent for the Demonstration Project. Based on this assumption, the Demonstration Project was predicted to reduce I/I in Basin BLS002 by a range of 1.8 million gallons per day (mgd) to 2.2 mgd. This reduction estimate was based on the assumption of rehabilitating only the laterals and side sewers. Additional reduction expected from replacement of sewer mains and manholes was not accounted for in the estimate. Achieving the lower end of the reduction range (60 percent) would provide sufficient downstream system capacity to eliminate the need for the Bryn Mawr Storage Facility.

Skyway Initial Infiltration and Inflow Reduction Demonstration Project Evaluation Report

### 1.2.3 Cost-Effectiveness

To evaluate cost-effectiveness, a benefit/cost ratio was calculated as follows:

CSI Project Savings After I/I Reduction

Benefit/Cost Ratio =

Cost of I/I Reduction Project

Projects with benefit/cost ratios greater than or equal to 1.0 are considered to be cost-effective. For the Skyway Demonstration Project, the benefit/cost ratio was calculated based on the County portion of the estimated project cost (the cost for rehabilitating the laterals and side sewers) and the projection that the project would allow for elimination of the Bryn Mawr Storage Project:

- Benefit—Avoided project cost for Bryn Mawr Storage Project: $5.37 million

- Cost—Estimated King County project cost for Skyway Demonstration Project: $5.62 million:

  - Total project cost consists of construction cost plus King County allied cost

  - This estimate is the pre-design estimate that was used at the time the cost-effectiveness evaluation was performed; the estimate was revised prior to project bid

- Benefit-to-cost ratio—0.95.

To increase the County’s benefit-to-cost ratio for the Demonstration Project to 1.0, the Skyway WSD planned to contribute $250,000 for lateral and side sewer rehabilitation, reducing the total cost to King County.

### 1.2.4 Identified Risks

A risk assessment of the proposed project was performed during predesign, based on the understanding of project conditions in the basin. Table 1-1 lists risks identified in the predesign report with medium or high impact potential and probability, along with their estimated risk costs and potential measures to mitigate the risks.

PROJECT OVERVIEW

TABLE 1-1. MEDIUM- AND HIGH-RATED RISK ELEMENTS AND MITIGATION MEASURES

Probability /Impact Risk Element Ratinga Potential Risk Mitigation / Response

Rights-of-entry are attained for too few low- M/H • Obtain sufficient rights-of-entry to allow for and medium-difficulty properties, requiring addition of properties to reach reduction targets. more work on high-difficulty properties, at a higher cost.

Too few rights-of-entry are attained to perform H/H • Obtain sufficient rights-of-entry to allow for the targeted amount of private property addition of properties to reach reduction targets. rehabilitation. Project cannot proceed to implementation.

I/I is not uniformly distributed across project M/H • Work in additional areas to get a greater I/I areas as assumed; and reduction targets are not reduction. achieved in the project area. • Could require multiple phases of construction over several years so that flows can be checked as rehabilitation work proceeds.

I/I removal targets in the basin are achieved; H/H • Work in additional areas to get a greater I/I however, a lesser reduction rate at the location reduction. of the downstream CSI project is realized • Could require multiple phases of construction because additional flows enter the system from over several years so that flows can be checked as other tributary areas rehabilitation work proceeds.

High bids M/M • Early timing for bids and award, before contractors are booked for upcoming construction season. Bid marketing, advance notice to contractors. Structure bid packages to allow for release of smaller packages to more contractors if necessary. a. M/M = Medium probability/medium impact; M/H = Medium probability/high impact; H/H = High probability/high impact

This page left Intentionally blank

# CHAPTER 2. FINAL DESIGN, BIDDING AND CONSTRUCTION

## 2.1 FINAL DESIGN

Final design for the Skyway Demonstration Project, completed in 2010, originally considered rehabilitation for 375 properties. Of these, about 25 were in the lower portion of the basin along Rainier Avenue South, a heavily traveled arterial roadway. These properties were omitted from the final work, due to the challenges of and cost and time associated with working in heavy traffic. The number of properties to be rehabilitated was further reduced based on whether rights of entry could be acquired from the property owners. Ultimately, 343 properties were included for rehabilitation in the final design.

An important bid item incorporated into the design for maintaining project flexibility during construction was the use of closed-circuit video inspection (CCTV) by the contractor prior to construction, to verify the side sewer alignments assumed in the design. The design of lateral and side sewer replacements drew upon information included in side sewer cards. Although the CCTV found that most of the information from the side sewer cards was accurate; some side sewer cards were found to be incorrect. Performance of the CCTV prior to construction allowed the correct alignments to be used in deciding whether to proceed with rehabilitation on each property.

In preparing bid documents, the design was based on unit costs for construction, rather than the lump sum bid approach typically used for King County construction projects. This approach provided greater flexibility during construction to add or remove properties from the project or to otherwise make changes based on unforeseen construction conditions.

## 2.2 BID RESULTS

The project was advertised for bid in December 2010 as two schedules: Schedule A for rehabilitation of the side sewers and laterals, and Schedule B for replacement of sewer mains and manholes. Six bids were received, and in March 2011 the contract was awarded to low bidder Buno Construction. This is the same contractor that constructed the 2003/2004 pilot project work. Table 2-1 summarizes the engineer’s estimate, average bid and low bid.

|  | TABLE 2-1. BID RESULTS |  |  |
| --- | --- | --- | --- |
| Description | Engineers Estimate | Average Bid Cost | Low Bid Cost |
| Schedule A – Side Sewers and Laterals | $3,157,000.00 | $2,609,377.28 | $1,253,387.50 |
| Schedule B – Sewer Mains and Manholes | $1,924,100.00 | $2,084,064.26 | $2,028,800.00 |
| Sales Tax Bid Schedule Subtotal Cost | $482,704.50 | $445,876.95 | $311,807.81 |
|  | $5,563,804.50 | $5,139,318.49 | $3,593,995.31 |

The low bid was substantially below the engineer’s estimate—low enough that no cost-sharing was required from the Skyway WSD for the Schedule A work. That left King County’s cost responsibility (for

Schedule A work) at $1.25 million plus tax and the Skyway WSD responsibility (for Schedule B work) at $2.03 million plus tax. The low bid seemed to further ensure a cost/benefit ratio of 1.0 or greater, as long as expected I/I reduction goals could be met.

The low bid differed from the engineer’s estimate and the other bids received in that it included more cost for Schedule B than for Schedule A. The low bidder may have assumed that portions of the planned lateral and side sewer replacement would be dropped from the contract based on field conditions following CCTV inspection. In fact, less than 70 percent of the lateral and side sewer pipe length identified in the final design was ultimately rehabilitated, as described in the next section.

## 2.3 CONSTRUCTION HIGHLIGHTS

### 2.3.1 Variations from Final Design

###### Schedule A – Side Sewers and Laterals

Laterals and side sewers were CCTV-inspected from the sewer main connection onto the private property immediately prior to work on each property. This allowed the sewer to be exactly located on the property, as a check of what was shown on the side sewer cards. Once the line was accurately located, an assessment was made of where pits would be required for pipe bursting and what surface features would be disturbed. The CCTV also allowed confirmation of the materials of side sewers on each property and whether a line was recently replaced, which would have already eliminated I/I from the line.

Decisions on the extent of rehabilitation for each property were made immediately following the CCTV work. Direction came from King County inspectors who monitored all construction activities for the duration of the project. Rehabilitation, if performed, followed within a day or two. Rehabilitation was ultimately performed on 298 of 343 properties included in the final design. The other 45 properties were omitted for one or more of the following reasons:

- CCTV revealed that the lateral and side sewer were recently replaced with PVC or other newer pipe material that appeared to be free from I/I (13 properties).

- The side sewer crossed beneath landscape or hardscape features such as rockeries, patios, entries or other improvements, making rehabilitation risky or overly difficult (20 properties).

- Property owner decided against rehabilitation after learning which landscape or hardscape features would be disturbed (4 properties).

- Property shared a common side sewer with one or more other properties that were not being replaced for any of the reasons above (8 properties).

Table 2-2 shows the quantity of lateral and side sewer pipe that was designed and bid for rehabilitation vs. how much was actually constructed. Less than 70 percent of side sewer and lateral pipe length that was bid was actually replaced. In addition to the 45 properties that were not rehabilitated at all, this difference between bid quantities and implementation quantities is attributable to properties where the level of replacement was stopped short of full completion. This is discussed further in Chapter 3.

###### Schedule B – Sewer Mains and Manholes

There were few uncertainties regarding main and manhole replacement under Schedule B, because good as-built information on the existing system was available and nearly the entire alignment could be CCTVinspected during project design. As shown in Table 2-3, 95 percent of the bid sewer main and 94% of manhole replacements were constructed.

Skyway Initial Infiltration and Inflow Reduction Demonstration Project Evaluation Report

| TABLE 2-2. SCHEDULE A SIDE SEWER AND LATERAL VARIATIONS |  |
| --- | --- |
| Example Bid Items | Bid Quantity | Final Quantity |
| Preconstruction CCTV of side sewers and laterals | 32,965 feet | 28,990 feet |
| Side sewer and lateral replacement by pipe bursting | 32,965 feet | 21,981 feet |
| Side sewer and lateral replacement by open cut | 500 feet | 1,300 feet |
| Lateral reconnections to sewer main | 374 | 345 |
| Cleanouts installed on side sewers | 472 | 371 |

| TABLE 2-3. SCHEDULE B SEWER MAIN AND MANHOLE VARIATIONS |  |
| --- | --- |
| Example Bid Items | Bid Quantity | Final Quantity |
| Preconstruction CCTV of sewer main | 21,400 feet | 20,630 feet |
| Sewer main replacement by pipe bursting | 21,400 feet | 20,369 feet |
| Manhole replacements | 99 | 93 |

### 2.3.2 Construction Challenges

###### Side Sewer Location and Connections on Private Property

Some side sewer connections on private property were found to be deeper than expected, making connection to the home difficult. Challenges also were faced when clearance constraints on private property made it difficult to place construction equipment as needed to reach sewer connection points. On many properties designated for rehabilitation, the side sewer was only partially replaced because extensive hardscapes or landscaping would have had to be removed or were at risk of being damaged.

###### Groundwater Issues Following Construction

Groundwater appeared around sites disturbed by construction, surfacing in alleys, in manhole excavations, at side sewer connection excavations in yards, and occasionally in pavement cracks above undisturbed trench lines. Because pipe bursting is primarily a trenchless option, it limits the possibility to install groundwater drainage concurrent with sewer installation.

###### Pavement Settling Occurred Above Sewer Main Trench Lines in the Right of Way

Pavement settlement occurred in a number of locations. This likely was due to groundwater, which was no longer infiltrating into the sewer system, following pipe-burst mains and causing settlement in the trench backfill of the original pipeline construction (see Figure 2-1). In one case, where there was a steep gradient down a roadway, groundwater traveling along the trench line actually broke surfaced through the asphalt (see Figure 2-2).

The largest cost of change orders on the project were related to addressing these groundwater issues in the right of way. Trench drains were constructed to mitigate the possibility of groundwater issues beneath pavement in high problem areas (see Figure 2-3). In some cases, additional or enlarged trench patch repairs were constructed.

Figure 2-1. Pavement Settlement Along Sewer Main Alignment Following Construction

Figure 2-2. Groundwater Following Burst Sewer Main Trench Breaks Out of Pavement Skyway Initial Infiltration and Inflow Reduction Demonstration Project Evaluation Report

Figure 2-3. Retrofit Trench Drain Captures Groundwater Flow and Alleviates Pavement Settlement

## 2.4 FINAL COSTS

The final construction cost was $3,417,625.50, somewhat below the low bid cost of $3,593,995.31 (both numbers with tax). Seven change orders included a total of $150,760.69 in additional costs. An eighth and final change order formalized the reduced unit quantities of $311,829.14. The reduced quantities were primarily related to fewer laterals and side sewers being rehabilitated.

## 2.5 WARRANTY INSPECTION

The County initiated the inspection of a representative sample of the constructed mains—13 sewer main segments totaling 2,800 feet of pipe and the adjoining manholes. The inspections were completed during the wet season in January 2013 using CCTV equipment. Inspection data included raw video footage of each pipe segment, selected still captures from the video footage, and summary inspection reports describing the pipeline observations, side sewers, evidence of I/I, and distances from upstream and downstream manhole numbers. Documented observations within the new sewer main initially included rock and other debris blockage problem sites, a vertical joint offset concern, and high water levels from sags and debris obstacles. The offset and sags are likely reflective of the original pipeline’s alignment. These inspection results were evaluated to determine conditions and whether additional warranty enforcement work was appropriate.

In subsequent communication, it was learned that some pipes with identified debris problems had been cleaned by the Skyway WSD after the video inspection. Also, there may have been upstream debris that migrated into the newly constructed pipes. An additional warranty CCTV inspection was therefore performed in the two pipe segments after the cleaning, resulting in the conclusion that no further cleaning of potential construction debris was necessary. A second CCTV inspection of a pipe joint vertical deflection was also completed, and the interior of the joint appeared to be tight and intact, with no evidence of outside debris or infiltration water entering through the joint.

It was concluded that all pipeline inspection issues of initial concern were reconciled and that no remaining issues merited warranty enforcement was merited. Overall, constructed conditions were as would be expected for construction using pipe burst methods. The completed conveyance system was recommended for acceptance.

# CHAPTER 3. PROJECT EFFECTIVENESS EVALUATION

A key objective of the Demonstration Project was to evaluate the effectiveness of sewer rehabilitation. Rainfall and flow data were evaluated to determine if rehabilitation reduced I/I enough to allow for delaying, reducing the size of, or eliminating the Bryn Mawr Storage Project. I/I reduction was quantified by comparing model results based on flow data collected before and after construction of the Demonstration Project (pre-rehabilitation and post-rehabilitation). The methodology is described in the appendix to this report.

## 3.1 BASIN DELINEATION AND MONITORING

### 3.1.1 Basin Boundaries and Flow Meter Locations

Pre-project modeling was based upon flow modeling completed after the pilot project. Flow monitoring following construction was conducted during the 2012/2013 wet season. Four hydrologic basins (see Figure 3-1) were initially delineated to evaluate I/I rehabilitation effectiveness:

- The 157-acre Skyway Basin BLS002 consists of the three colored areas shown in Figure 3-1 (green, blue and orange). Rehabilitation work as part of the Demonstration Project was performed only in the green and blue highlighted portions of the basin, covering 111 acres.

- The 46-acre Skyway Pilot Basin (shown in orange in Figure 3-1) is the area that was rehabilitated during the 2003/2004 Skyway pilot project. The area is tributary to downstream Flow Meter BLS002 and was monitored to assess the level of I/I remaining in this previously rehabilitated portion of the system. No rehabilitation work was performed in this area of the basin during the Demonstration Project.

- The 38-acre Skyway Control Basin (shown in blue in Figure 3-1) was established at the time of the 2003/2004 Skyway pilot project to define baseline conditions without I/I rehabilitation, for comparison with the Skyway Pilot Basin. It was monitored before and after the 2003/2004 Skyway pilot project, concurrently with the Skyway Pilot Basin, and the results were compared to verify that flow reductions in the Skyway Pilot Basin were a result of the rehabilitation work. For the Demonstration Project, rehabilitation was performed in the Skyway Control Basin.

- The 506-acre Model Basin M_BLS43B (see the Figure 3-1 inset) covers multiple basins acres, including BLS002. The outlet from this basin is the location where the peak flow reduction of 1.8 mgd must be attained to eliminate the need for the Bryn Mawr storage facility.

Flows from these basins were monitored at the following flow-meter locations, which are shown on Figure 3-1:

- Pilot Flow Meter at the downstream end of the Skyway Pilot Basin

- Control Flow Meter at the downstream end of the Skyway Control Basin

- BLS002 Meter at the downstream end of Skyway Basin BLS002

- BLS43B Meter at the downstream end of Model Basin M_BLS43.

Figure 3-1. BLS002 Demonstration Project Basin Boundary with Meter Locations

### 3.1.2 Basin Boundary Issues

When post-rehabilitation flow monitor locations were being established, a previously unrecognized flow diversion was identified, contributing flow to the Skyway Basin BLS002 from the area immediately to the south. The area is shown as the 148F Basin in Figure 3-2. Prior to the Demonstration Project construction, flow from the 148F Basin entered a manhole near the intersection of South 112th Street and 80th Avenue South. Low flows were routed to Basin BLS006, immediately south of BLS002. As flow rates increased during periods of wet weather, some of the flow from the 148F Basin was diverted east along South 112th Street, to the Skyway Basin BLS002 system.

The manhole containing this flow diversion was removed during construction of the Demonstration Project, at the direction of Skyway WSD staff, and all flow from the 148F Basin now flows through the Skyway Basin BLS002 system; the area is therefore now part of Skyway Basin BLS002. The 148F Basin covers 62 acres and includes 240 homes. Following discovery of this basin boundary issue, an additional meter (148F Flow Meter) was installed to record flows from the area and factor them into the project effectiveness evaluation. The meter location is shown on Figure 3-2.

Figure 3-2. Connected Basin 148F

## 3.2 MODELING

Data collected during the 2012/2013 wet-weather post-rehabilitation flow monitoring was input into the County’s MOUSE hydrologic model to estimate the I/I remaining in Skyway Basin BLS002 and Modeling Basin M_BLS43B, and assess the effectiveness of the I/I removal efforts. The modeling included the following elements:

- Collection of rainfall and evaporation records

- Characterization of dry-weather flow

- Calibration of the hydrologic model for the monitoring period

- Simulation of an extended time series to process results into flow events and develop peak 20-year I/I.

Pre-rehabilitation modeling results were compared to the post-rehabilitation modeling results to calculate the I/I removal effectiveness of the Demonstration Project.

## 3.3 I/I REDUCTION EFFECTIVENESS RESULTS

### 3.3.1 Flow Reduction by Basin

Table 3-1 summarizes I/I removal effectiveness. For the Demonstration Project, peak I/I was reduced by 0.6 mgd in the Control Basin, a 48-percent reduction. At the BLS002 Flow Meter, peak I/I was reduced by 0.78 mgd, or 19 percent. At the BLS043B meter, no reduction in peak I/I was seen. The estimated peak post-rehabilitation flows calculated for this location were a bit higher than the pre-rehabilitation values, by about 3 percent. These results fell well short of the reductions predicted during the project design.

TABLE 3-1. REMOVAL EFFECTIVENESS BASED ON POST-PROJECT FLOW MONITORING

Peak 20-Year I/I

Pilot Control BLS002 BLS043B Meter Meter Meter Meter

Demonstration Project Effectiveness Pre-Demonstration Project 0.25 mgd 1.24 mgd 4.07 mgd 11.05 mgd Post-Demonstration Project 0.25 mgd 0.64 mgd 3.29 mgd 11.43 mgd Percent Reduction N/A 48% 19% -3%

Pilot Project Effectiveness Pre-Pilot Project 2.15 mgd 1.24 mgd 5.97 mgd 12.62 mgd Post-Pilot Project 0.25 mgd 1.24 mgd 4.07 mgd 11.05 mgd Percent Reduction 89% N/A 32% 13%

For comparison purposes, the reduction effectiveness of the 2003/2004 Skyway pilot project is also listed in Table 3-1. Following completion of that construction, peak I/I in the Skyway Pilot Basin was reduced by 1.9 mgd, a reduction of 89 percent. The same 1.9-mgd reduction in I/I was registered downstream at the BLS002 Meter, representing a 32-percent reduction for the entire basin. At the BLS043B Meter, peak I/I was reduced slightly less, by 1.6 mgd, representing a 13-percent reduction for the modeling basin.

Flows at the Pilot Basin boundary were also measured as part of the Demonstration Project to confirm the ongoing effectiveness of the previous I/I reduction measures. The new monitoring shows that I/I remains controlled in this area, with a peak calculated 20-year I/I value of 0.25 mgd.

### 3.3.2 I/I During a Selected Storm Event

Figure 3-3 shows measured flow at each meter location for a particular rainfall event that occurred during the post-rehabilitation monitoring period. The hydrograph helps demonstrate where I/I remains in the area. The red line represents the flow measured at the BLS002 Meter. For this event, there was a peak flow of approximately 2.2 mgd. The other lines on the graph represent how flows were apportioned within Skyway Basin BLS002:

- The green and blue lines indicate flows in the area where rehabilitation work was performed for the Demonstration Project.

- The orange line indicates flow from the previously rehabilitated Skyway Pilot Basin,

- The purple line indicates flow from the 148F Basin, where no rehabilitation work occurred.

Figure 3-3. Flow by Basin Area for Post-Rehabilitation Storm Event in January 2013

Flows from the Skyway Pilot Basin and the Skyway Control Basin represent a small percentage of the post-rehabilitation I/I flows in Skyway Basin BLS002. About one-third of the remaining I/I can be attributed to the lower end of the Demonstration Project area (green), and about one-half to 148F Basin where no rehabilitation work was performed. Each of these areas had peak flows of nearly 1.0 mgd for the monitored event.

While approximately equal portions of I/I appear to remain in the green and purple areas of the basin, the response of the I/I is quite different between the two areas. In the purple area, the rapid rise and fall of the hydrograph in unison with the rainfall is typical of flow patterns attributable to leaky side sewers. The rise and drop-off of flows from the green area is much more gradual. This could indicate infiltration into portions of the sewer system that were not rehabilitated, especially in lower portions of the basin where groundwater is higher. These lower areas also may experience I/I that has migrated from rehabilitated system areas where it is no longer able to enter the sewers. The gradual response also may be the result of sump pumps in this lower portion of the basin where groundwater impacts are more pronounced.

## 3.4 I/I REDUCTION EFFECTIVENESS SUMMARY

The reduction effectiveness of the Skyway I/I Reduction Demonstration Project is strongly counter to project expectations, even after accounting for the flow contribution from the 148F Basin. That area accounts for nearly half of the post-rehabilitation I/I remaining in the project area, but the I/I reduction in the delineated project area for the Demonstration Project was still far below the expected 60-percent removal. The 2003/2004 Skyway Pilot Project achieved an I/I reduction of 89 percent in the area where work was performed, and the Demonstration Project had strong similarities to the Pilot Project:

- The neighborhood was of the same age of construction with similar sewer system materials.

- The same design and pipe bursting replacement concept were used.

- The same contractor performed the rehabilitation on both projects.

- The same inspector observed construction on both projects.

The sections below describe factors that may have influenced I/I reduction effectiveness from the Demonstration Project.

### 3.4.1 Effect of Sump Pumps and Foundation Drains

Foundation drains and sump pumps in the Demonstration Project area might contribute flow to the sewer system that negates reduces the effectiveness of I/I rehabilitation measures. Side sewers that collect I/I effectively act as drains to remove groundwater from the property. When those sewers have been rehabilitated and no longer convey I/I, the groundwater may increase against the house foundations, causing more flow to foundation drains and sumps. Direct and indirect evidence indicates a number of private property connections discharging to the sanitary sewer from inside the foundation walls. No sump pumps or foundation drains were disconnected from the sewer system as part of this project.

### 3.4.2 Groundwater at Sewers Downslope of Improved Area

When side sewers were stopped from behaving as groundwater drains, the groundwater level may have become temporarily amplified in areas downslope of the rehabilitated sewers, depending on soils and topography. This could cause higher infiltration pressures on unimproved sewer facilities in those downslope areas. The susceptible unimproved sewers could even include portions of the side sewer system and building plumbing that are within the footprint of homes, especially those with crawl spaces where drainage is a concern.

### 3.4.3 Incompletely Rehabilitated Properties

The ideal project on each rehabilitated property would replace the entire side sewer and lateral from the main sewer in the street to the extension of the internal plumbing (often cast iron pipe) outside the footprint of the house. However, conditions on individual properties can prohibit replacement of that entire sewer length. Where less than 75 percent of the line was replaced, the work was designated as a “partial” rehabilitation. In the 2003/2004 Skyway Pilot Project, total rehabilitation was completed on almost all properties included in the final design. For the Demonstration Project, many more properties were only partially rehabilitated. The final rehabilitation work was categorized as follows (see Figure 3-4):

- Total or Near Total Side Sewer Replacement (224 Properties)—Replacement of 75 percent or more of the total length of side sewer and lateral.

- Partial Side Sewer Replacement (72 Properties)—Replacement of less than 75 percent of the total length of side sewer and lateral. Partial replacements resulted almost exclusively from constructability constraints due to the location of side sewer in relation to property improvements, such as decks and patios.

- No Side Sewer Replacement (79 Properties)—The final design omitted 32 properties in the project area, primarily because rights-of-entry could not be attained or because the side sewer and lateral for the property had already been replaced within the last 10 years. Another 45 properties were not rehabilitated for the reasons described in Section 2.3.1.

Figure 3-4. Side Sewer Replacement Status

Figures 3-5 and 3-6 provide an example of a site where a full replacement was called for in the contract documents but field conditions dictated a modified plan. Figure 3-5 shows the replacement that was originally designed for five properties that shared a single lateral connection to the sewer main. Between the two homes near the connection to the main (10867/10873) and the three properties to east (10948/10950/10954) the contractor was to burst the existing 6-inch line and pull three separate 4-inch side sewers so that these three homes would each be on an individual dedicated side sewer. It was discovered during construction that multiple utilities cross the 6-inch line between the homes. These utilities were at risk of being damaged by pipe-bursting of the existing line. The decision was therefore made not to replace this approximately 100-foot section of line. The length of line actually replaced is shown on Figure 3-6 and is representative of a partial sewer replacement.

### 3.4.4 Diminished Effectiveness Downstream From Project

The Demonstration Project’s effectiveness as measured at different flow meters suggests that I/I reduction benefits may not extend far downstream from the immediate area where rehabilitation is performed:

- Peak I/I was reduced by 0.6 mgd at the Control Meter, representing the benefit of Skyway Control Basin rehabilitation in the work area immediately upstream of that meter.

- Because the BLS002 Meter measures all flow from the Skyway Control Basin plus additional area with more rehabilitated properties than were in the Control Basin, it would be reasonable to expect I/I reduction on the order of double what was measured at the Control Meter. This would assume the same proportion of side sewer replacement occurred in both areas, but Figure 3-4 shows that is not the case. The measured I/I reduction at the BLS002 Meter was 0.78 mgd—only slightly greater than the 0.6 mgd measured at the Control Meter. This suggests the full benefit of work in the Control Basin may not have extended downstream to the BLS002 Meter.

Figure 3-5. Full Side Sewer Rehabilitation as Designed

Figure 3-6. Partial Side Sewer Rehabilitation as Constructed

- Further downstream, at the BLS043B Meter, the post-project peak I/I is about the same as the pre-project value; so it appears that none of the benefit of the project extended that far downstream.

Overall, these results suggest that the benefits of rehabilitation work are most apparent in the local system where the work is performed and that downstream translation of I/I reduction is more difficult to achieve.

### 3.4.5 Impact on Need for Other Capital Projects

The goal of the Demonstration Project in Skyway was to delay, downsize, or eliminate the need for the Bryn Mawr Storage Project. While this project has not demonstrated that the storage project can be eliminated, it does appear that it can be delayed. Further, the rehabilitation work may have led to a reduction in required storage volume despite the slightly higher peak flow rate due to a change in shape of the hydrograph (narrowing of the peak flow portion of the curve). These positive results were achieved with a capital cost to King County of less than $2 million. The County will continue with flow monitoring in Skyway and elsewhere and will consider future I/I reduction projects where they may be of value.

# CHAPTER 4. LESSONS LEARNED

Extensive work went into development, implementation and evaluation of the Skyway I/I/ Reduction Demonstration Project—from pilot testing in 2003 through project evaluation completed with this report. The following sections summarize general lessons learned from the process that can be used to guide design and construction of future I/I reduction projects in King County.

## 4.1 DESIGN

### 4.1.1 Identifying Problem Areas

An essential first step in developing an I/I reduction project is the identification of geographical areas where I/I is entering the sewer system in quantities that can be cost-effectively reduced. Sources of infiltration to a collection system can seldom be pinpointed with certainty or precision. The work leading up to the Skyway Demonstration Project found that an acceptable approach to identifying suitable areas for I/I/ reduction is to compare a basin’s peak I/I flow to its population density. A rule of thumb developed during the alternatives analysis for initial I/I reduction projects is that, in residential areas, a peak I/I flow equivalent to an average of 3 gallons per minute or more from each property is a good indicator of where to focus rehabilitation efforts.

### 4.1.2 Basin Characterization

Typical gravity sewer collection systems are branched networks with discrete boundaries. In practice, however, conditions in aging sewer systems are impacted by decades of degradation, sedimentation, grease accumulations, and modifications by homeowners or contractors. Lost or incomplete records from years past can impact the ability to clearly define the configuration of the sewer system in a study area. A thorough assessment of physical conditions and a comparison to records are important to defining basin boundaries and selecting flow meter locations for optimal hydraulics. This is in addition to sewer system evaluation survey activities such as cleaning, CCTV and smoke testing. Those activities may not, by themselves, provide all the information necessary. Additional investigation is appropriate, especially at the basin periphery and at connections with adjacent basins.

### 4.1.3 Design Certainty and Priority of Project Expenditures

By the nature of the work involved, I/I reduction projects pose challenges to the development of a precise and accurate design. It will seldom be possible to identify in advance, with any degree of certainty, the locations of significant I/I flows or the private property conditions that can affect construction. The inability of the Demonstration Project to match the I/I reduction achieved by the Skyway Pilot Project, despite the strong similarities in project area and approach, brings into question the ability to develop I/I reduction project designs with a high degree of certainty and points to differences between the Pilot and Demonstration projects.

For the Skyway Demonstration Project, assumptions were made about the project area to simplify the design effort—such as the assumption that the level of I/I is uniformly distributed across the basin. While this is obviously a simplification, developing a more detailed distribution of I/I levels across a basin would require flow data from significantly more locations within the basin, at a high cost. Such prolonged and expensive investigations and design work may not be an effective use of project funding. Rather, the

LESSONS LEARNED

focus should be on an efficiently developed design that leaves funding available to modify work as needed during construction.

### 4.1.4 Consideration of Sump Pumps

Based on the findings of the effectiveness evaluation for the Demonstration Project, it is recommended that design of an I/I reduction project take into account the prevalence of foundation sump pumps discharging into the sewer system. The likely effect of sump pumps on I/I removal effectiveness should be considered greater when the following conditions are noted:

- High groundwater is already a documented or anecdotal problem in the neighborhood

- High percentage of full or daylight basements

- Observations of periodic clean, cold water discharge noted in side sewer(s), reportedly when no one was home

## 4.2 CONSTRUCTION

### 4.2.1 Flexibility

Given the complexity of preparing accurate, detailed designs for I/I reduction projects, construction should be implemented with maximum potential for modifying the design as needed based on conditions encountered in the field. During the Skyway Demonstration Project an owner’s representative was constantly available for field decision-making. Contract documents also provided flexibility for private property work, through a separate bid item for CCTV, which allowed field determination of the appropriate extent of side sewer replacement based on considerations of equipment clearance and hardscape and landscaping constraints. Structuring the contract with unit prices allows for deleting or adding work on individual properties.

### 4.2.2 Performance-Based Scheduling

Tighter performance-based restoration scheduling should be used for private property side sewers. Contract documents for the Demonstration Project required notification to homeowners prior to construction disturbances and defined the method of notification, but no time limit was set as to how soon after construction restoration must be substantially completed. A performance schedule strategy should suggest options, including the number of crews, etc., but should avoid prescribing means and methods.

### 4.2.3 Groundwater Issues

Based on conditions encountered during the Demonstration Project, I/I reduction projects should anticipate the possibility of groundwater issues that may follow disturbed ground associated with pipe bursting, open trenching and manhole and side sewer connections. Projects should consider the possibility of groundwater interception and discharge methods to function as groundwater pressure relief points, discharging to storm drain collection systems. Coordination with the respective roadway and/or drainage agency is helpful.

If groundwater interception and discharge methods are applicable, they should be limited to strategic locations in the collection system already disturbed by construction activities, such as junction manholes at intersections and side sewer connections at the base of steep streets.

Skyway Initial Infiltration and Inflow Reduction Demonstration Project Evaluation Report

### 4.2.4 Contingency Bid items

I/I reduction project documents should include contingency bid items or funding for unusual or unexpected side sewer route adjustments drainage problems, landscape restoration, hardscape restoration, or other unintended consequences.

##### 4.2.5 Side Sewer Replacement

Reasonable measures should be taken, to the extent they are cost-effective, to replace as much of side sewers as possible.

##### 4.2.6 Foundation Drains

Explore the possibility of routing foundation drains into the storm system.