2012 King County

Long-term Combined Sewer Overflow Control Plan Amendment

October 2012

Department of Natural Resources and Parks

Wastewater Treatment Division

Combined Sewer Overflow Control Program

King Street Center, KSC-NR-0512

201 South Jackson Street

Seattle, WA  98104

http://www.kingcounty.gov/environment/wastewater/cso.aspx

For comments or questions, contact:

Karen Huber, CSO Control Program Manager

King County Wastewater Treatment Division

201 South Jackson Street

KSC-NR-0512

Seattle, WA  98104-3856 206-684-1246 karen.huber@kingcounty.gov

This information is available in  alternative formats on request at 206-684-1242 (voice) or 711 (TTY) Contents

Transmittal letter: Submittal of King County's 2012 Long-term CSO Control Plan Amendment, October 18, 2012

King County Ordinance 17413

2012 CSO Control Program Review Report, Revised August 2012

2012 CSO Control Program Review Report

June 2012

Revised August 2012

Department of Natural Resources and Parks

Wastewater Treatment Division

Combined Sewer Overflow Program

King Street Center, KSC-NR-0512

201 South Jackson Street

Seattle, WA  98104

http://www.kingcounty.gov/environment/wastewater/cso.aspx

For comments or questions, contact:

Karen Huber, CSO Control Program Manager

King County Wastewater Treatment Division

201 South Jackson Street

KSC-NR-0512

Seattle, WA  98104-3856 206-684-1246 karen.huber@kingcounty.gov

This information is available in  alternative formats on request at 206-684-1242 (voice) or 711 (TTY)

Table of Contents

Executive Summary .............................................................................................................................. ES-1

Report Purpose ............................................................................................................................ ES-1 Background ................................................................................................................................. ES-2 Uncontrolled King County CSO Sites ........................................................................................ ES-4 CSO Control Program Review Approach ................................................................................... ES-7 Alternative Evaluation Methodology .......................................................................................... ES-7 Recommended Preferred Alternatives ........................................................................................ ES-8 Schedule, Rate Forecasting, and Affordability ........................................................................... ES-8 Public Review and the King County Executive’s Recommended CSO Control Plan ................ ES-9

King County Council Review and Long-term CSO Control Plan Amendment Adoption ........ ES-11

Chapter 1 	Introduction ....................................................................................................................... 1-1

1.1 	Definition of CSOs .............................................................................................................. 1-2

1.2 	Purpose of the County’s Program Review ........................................................................... 1-2

1.3 	King County’s Role in Wastewater Management ............................................................... 1-6

1.4 	Purpose of CSO Control ...................................................................................................... 1-7

1.4.1 Public Perception and Preferences Regarding CSOs ............................................... 1-7

1.4.2 King County CSO Control Policies ......................................................................... 1-8

1.4.3 Applicable Water Quality Regulations .................................................................... 1-9

1.4.4 CSO Control Regulations ....................................................................................... 1-10

1.4.5 Sediment Quality Regulations ............................................................................... 1-10

1.4.6 Endangered Species Act ......................................................................................... 1-11

1.5 	King County Efforts to Control CSOs ............................................................................... 1-12

1.6 	CSO Sites Covered by Current Review ............................................................................. 1-17

1.7 	Relationship Between King County and City of Seattle CSO Control Efforts .................. 1-19

1.8 	Ecology and EPA Report Requirements ............................................................................ 1-20

1.9 	Report Outline ................................................................................................................... 1-28 Chapter 2 	History of CSO Control .................................................................................................... 2-1

2.1 	CSO Control Planning Prior to the 1999 Plan Amendment ................................................ 2-1

2.2 	CSO Control Planning in the 1999 Plan Amendment ......................................................... 2-3

2.2.1 1999 CSO Control Planning Assumptions ............................................................... 2-3

2.2.2 CSO Control Projects Identified in the 1999 Plan Amendment ............................... 2-3

2.3 	CSO Control Program Review and Plan Updates ................................................................ 2-5

2.3.1 2000 CSO Control Plan Update ............................................................................... 2-5

2.3.2 2006 CSO Control Program Review ........................................................................ 2-6

2.3.3 2008 CSO Control Plan Update ............................................................................... 2-6 2.3.4 2012 CSO Control Program Review ........................................................................ 2-6

2.4 	Additional Planning and Environmental Review ................................................................ 2-7 Chapter 3 	King County’s Current CSO Control Program ............................................................. 3-1

3.1 	Measuring Progress in CSO Control ................................................................................... 3-1

3.1.1 Ecology’s CSO Control Performance Standard ....................................................... 3-1

3.1.2 Defining an Overflow Event .................................................................................... 3-1

3.1.3 CSO and Rainfall Monitoring .................................................................................. 3-2

3.1.4 CSO Modeling ......................................................................................................... 3-3

3.2 	CSO Control Approaches .................................................................................................... 3-3

3.2.1 Operational Controls ................................................................................................ 3-4

3.2.2 CSO Treatment ........................................................................................................ 3-5

3.2.3 Pollution Prevention and Source Control ................................................................. 3-6

3.2.4 EPA CSO Control Policy Nine Minimum Controls ................................................ 3-7

3.3 	Projects to Control CSOs ................................................................................................... 3-13

3.4 	Results of CSO Control Program to Date .......................................................................... 3-16

3.5 	Supplemental Compliance Plans ....................................................................................... 3-18

3.6 	Reporting on CSO Control ................................................................................................ 3-19

3.7 	Control Plan Review and Amendment .............................................................................. 3-20 Chapter 4 	Factors Considered in Current CSO Control Program Review ................................... 4-1

4.1 	Regulatory and County Policy Factors ................................................................................ 4-2

4.1.1 Water Quality Regulations ....................................................................................... 4-2

4.1.2 Sediment Management ............................................................................................. 4-3

4.1.3 EPA Policy Compliance ........................................................................................... 4-4

4.1.4 County Policy Factors .............................................................................................. 4-6

4.1.5 1999 Plan Amendment Alternatives Needing Review Due to Regulatory and

County Policy Changes ............................................................................................ 4-6

4.2 	Technical Factors ................................................................................................................. 4-7

4.2.1 Characterization of the King County Service Area .................................................. 4-7

4.2.2 Size and Type of CSO Control Facility from Hydraulic Modeling ....................... 4-13

4.2.3 Performance of Existing CSO Controls and Changes in CSO Treatment

Technologies .......................................................................................................... 4-15

4.2.4 Green Stormwater Infrastructure (GSI) ................................................................. 4-18

4.2.5 Siting of CSO Control Facilities ............................................................................ 4-19

4.2.6 Asset Management ................................................................................................. 4-20

4.2.7 1999 Plan Amendment Alternatives Needing Review Due to Technical Factor

Changes .................................................................................................................. 4-21

4.3 	Human and Environmental Health Factors ........................................................................ 4-22

4.3.1 Recent Science ....................................................................................................... 4-22

4.3.2 Habitat Restoration ................................................................................................ 4-26

4.3.3 Sensitive Areas ....................................................................................................... 4-26

4.3.4 CSO Control Priority Conclusions ......................................................................... 4-28

4.3.5 1999 Plan Amendment Alternatives Needing Review Due to Human and

Environmental Health Factor Changes .................................................................. 4-29

4.3.6 Change Following 2011 WTD Recommended CSO Control Plan Public

Involvement ........................................................................................................... 4-29

4.4 	Public and Regulatory Agency Participation ..................................................................... 4-29

4.4.1 1999 Plan Amendment Alternatives Needing Review Due to Public and Regulatory

Agency Participation Changes ............................................................................... 4-31

4.5 	Coordination with Other Agencies .................................................................................... 4-32

4.5.1 City of Seattle’s CSO Control Program ................................................................. 4-32

4.5.2 Other Agencies ....................................................................................................... 4-34

4.5.3 1999 Plan Amendment Alternatives Needing Review Due to Agency Coordination

Changes .................................................................................................................. 4-34

4.6 	Summary of Need for Alternative Re-Evaluation ............................................................. 4-35 Chapter 5 	Alternatives Development, Evaluation, and Selection ................................................... 5-1

5.1 	Evaluation Overview ........................................................................................................... 5-1

5.1.1 Terminology ............................................................................................................. 5-1 5.1.2 Evaluation Process ................................................................................................... 5-2

5.2 	Feasible CSO Control Approaches ...................................................................................... 5-5

5.3 	Preliminary Alternatives ...................................................................................................... 5-7

5.3.1 Identification of Preliminary Alternatives ............................................................... 5-7

5.3.2 Screening of Preliminary Alternatives ..................................................................... 5-9

5.4 	Final Alternatives ............................................................................................................... 5-11

5.4.1 Description of Final Alternatives ........................................................................... 5-11

5.4.2 Planning-Level Design Criteria ............................................................................. 5-13

5.5 	Triple-Bottom-Line Analysis Process ............................................................................... 5-14

5.5.1 Steps in Triple-Bottom-Line Analysis ................................................................... 5-15

5.5.2 Identification of Preferred Alternatives ................................................................. 5-18

5.6 	Recommending Preferred Alternatives .............................................................................. 5-20

5.6.1 Ship Canal—11th Ave NW, 3rd Ave W, University and Montlake ...................... 5-20

5.6.2 Middle Elliott Bay Interceptor (MEBI)—Hanford #2, Lander St, Kingdome, and

King St ................................................................................................................... 5-24

5.6.3 Middle Elliott Bay Interceptor—Hanford #1 ......................................................... 5-28

5.6.4 South Elliott Bay Interceptor ................................................................................. 5-30

5.6.5 West Duwamish—W Michigan St and Terminal 115 ........................................... 5-32

5.6.6 West Duwamish—Chelan Ave .............................................................................. 5-34

5.7 	Green Stormwater Infrastructure Evaluation ..................................................................... 5-36

5.8 	Agency Approval ............................................................................................................... 5-43 Chapter 6 	Recommended Preferred Alternatives ............................................................................ 6-1

6.1 	Ship Canal—11th Ave NW, 3rd Ave W, University, and Montlake ................................... 6-3

6.1.1 Recommended Preferred Alternative ....................................................................... 6-3

6.1.2 Potential Risks, Issues, and Additional Considerations ........................................... 6-4

6.2 	Middle Elliott Bay Interceptor—Hanford #2, Lander St, Kingdome, and King St ............. 6-7

6.2.1 Recommended Preferred Alternative ....................................................................... 6-7

6.2.2 Potential Risks, Issues, and Additional Considerations ........................................... 6-7

6.3 	Middle Elliott Bay Interceptor—Hanford #1 ....................................................................... 6-8

6.3.1 Recommended Preferred Alternative ....................................................................... 6-8

6.3.2 Potential Risks, Issues, and Additional Considerations ........................................... 6-8

6.4 	South Elliott Bay Interceptor ............................................................................................... 6-8

6.4.1 Recommended Preferred Alternative ....................................................................... 6-8

6.4.2 Potential Risks, Issues, and Additional Considerations ........................................... 6-9

6.5 	West Duwamish—W Michigan St and Terminal 115 ......................................................... 6-9

6.5.1 Recommended Preferred Alternative ....................................................................... 6-9

6.5.2 Potential Risks, Issues, and Additional Considerations ........................................... 6-9

6.6 	West Duwamish—Chelan Ave .......................................................................................... 6-10

6.6.1 Recommended Preferred Alternative ..................................................................... 6-10

6.6.2 Potential Risks, Issues, and Additional Considerations ......................................... 6-10 Chapter 7 	Project Sequence Evaluation ............................................................................................ 7-1

7.1 	Project Sequence Evaluation ............................................................................................... 7-1

7.1.1 Project Sequence Definition ..................................................................................... 7-1

7.1.2 Project Implementation Building Blocks ................................................................. 7-2

7.1.3 Initial Project Sequence Alternatives ....................................................................... 7-3

7.1.4 Evaluation Process ................................................................................................... 7-7

7.1.5 2011 WTD Recommended CSO Control Plan Project Sequence ............................ 7-8

7.1.6 King County Executive’s Recommended CSO Control Plan Project Sequence and

Water Quality Assessment and Monitoring Study ................................................... 7-9 Chapter 8 	Rate Analysis and Financing the Plan ............................................................................. 8-1

8.1 	Methodology for Rate Impact Analysis ............................................................................... 8-1

8.2 	Comparison of Initial Project Sequence Alternatives .......................................................... 8-3

8.2.1 Annual Expenditures ................................................................................................ 8-3

8.2.2 Rate Impacts ............................................................................................................. 8-4

8.3 	WTD-Recommended Project Sequence with Three Alternative Completion Dates ........... 8-7

8.3.1 Annual Expenditures ................................................................................................ 8-9

8.3.2 Rate Impacts ........................................................................................................... 8-10

8.4 	King County Executive’s Recommended Project Sequence with 2030 Completion Date 8-13

8.4.1 Rate Impacts ........................................................................................................... 8-14

8.5 	Affordability of King County Executive’s Recommended CSO Control Plan and Financial

Capability to Fund the Plan ............................................................................................... 8-14

8.5.1 Economic Indicators .............................................................................................. 8-15

8.5.2 Other Considerations .............................................................................................. 8-20

8.5.3 Conclusions ............................................................................................................ 8-25

Chapter 9 	System Operational Plan .................................................................................................. 9-1

Chapter 10 King County’s Long-term  CSO Control Plan and  Recommended Amendment .... 10-1

10.1 Planned Projects Currently Underway ............................................................................... 10-1

10.2 Future Projects in the King County Executive’s Recommended CSO Control Plan ......... 10-1

Chapter 11 Next Steps ........................................................................................................................ 11-1

11.1 2012 CSO Control Program Review Report and King County Executive’s

Recommended CSO Control Plan ..................................................................................... 11-1

11.2 2012 Long-term CSO Control Plan Amendment ............................................................... 11-1

11.3 Implementation of Water Quality Assessment and Monitoring Study .............................. 11-1

11.4 Post-Construction Monitoring and Compliance with Water Quality Standards ................ 11-2

List of Figures

Figure ES-1. King County 2012 Long-term CSO Control Plan Amendment Process ......................... ES-1 Figure ES-2. King County and City of Seattle CSO Locations ............................................................ ES-3

Figure ES-3. Historical Reduction in Volumes Since Construction of the Regional System

(1958-79) and CSO Control (1979-Present) .................................................................... ES-5

Figure ES-4. King County CSO Site and Program Review Areas ....................................................... ES-6

Figure ES-5. Project Sequence and Schedule in King County Executive’s Recommended CSO

Control Plan ................................................................................................................... ES-11

Figure 1-1. King County 2012 Long-term CSO Control Plan Amendment Process ............................ 1-1 Figure 1-2. King County Wastewater Service Area and System .......................................................... 1-4 Figure 1-3. King County and City of Seattle CSO Locations ............................................................... 1-5

Figure 1-4. 	Historical Reduction in Volumes Since  Construction of the Regional System

(1958-79) and CSO Control (1979-Present) ..................................................................... 1-13

Figure 1-5. King County CSO Sites and Areas ................................................................................... 1-18 Figure 2-1. Past and Future CSO Control Planning .............................................................................. 2-1 Figure 3-1. Example of Defining CSO Events Using a 24-Hour Inter-Event Interval ......................... 3-2 Figure 4-1. Factors that Shape CSO Control Plan Decisions ................................................................ 4-2 Figure 4-2. Total RWSP and Updated Population Forecasts by Basin (2000 to 2050) ........................ 4-8 Figure 4-3.   Original RWSP and 2003 System-wide AWWF Projections .............................................. 4-11 Figure 4-4. Sample Process Flow Schematic for CEPT with Lamella Plates ..................................... 4-16 Figure 4-5. Sample Process Flow Schematic for Ballasted Sedimentation ......................................... 4-17 Figure 5-1. Identification and Evaluation of CSO Control Alternatives ............................................... 5-4 Figure 5-2. Risk Assessment Framework ........................................................................................... 5-17 Figure 5-3. Example of Alternative Screening Bracket (W Michigan St and  Terminal 115) ............ 5-18 Figure 5-4. Sample Scatter Graph for Identifying Preferred Site Alternative ..................................... 5-19 Figure 5-5. Site Alternatives for Ship Canal—11th Ave NW, 3rd Ave W, University, Montlake ..... 5-21 Figure 5-6. Area Alternatives for Ship Canal—11th Ave NW, 3rd Ave W, University, Montlake ... 5-23 Figure 5-7. Area Alternatives for Middle EBI—Hanford #2, Lander St, Kingdome, King St ........... 5-26

Figure 5-8. Site/Area Alternatives for Middle EBI—Hanford #1 ....................................................... 5-29 Figure 5-9. Brandon St Site Alternatives and South EBI Area Alternatives ....................................... 5-31 Figure 5-10. Area Alternatives for West Duwamish—W Michigan St and Terminal 115 ................... 5-33 Figure 5-11. Site/Area Alternatives for West Duwamish—Chelan Ave .............................................. 5-35 Figure 5-12. Uncontrolled CSO Basins Recommended for GSI ........................................................... 5-38 Figure 6-1. King County CSO Site and Areas ...................................................................................... 6-2 Figure 7-1. Assumed Timelines for Project Building Blocks ............................................................... 7-2 Figure 7-2. Duwamish River Cleanup Coordination Project Sequence Alternative ............................. 7-4 Figure 7-3. GSI-First Project Sequence Alternative ............................................................................. 7-5 Figure 7-4. Meet-SPU-Schedule Project Sequence Alternative ............................................................ 7-6 Figure 7-5. Joint-Tunnel Project Sequence Alternative ........................................................................ 7-7 Figure 7-6. WTD-Recommended Project Sequence ............................................................................. 7-8

Figure 7-7. 	King County Executive’s Recommended Project Sequence and Schedule with Water

Quality Assessment and Monitoring Study ...................................................................... 7-10

| Figure 8-1. | Annual Capital Expenditures for Initial Project Sequence Alternatives (2010 Dollars) .... 8-4 |
| --- | --- |
| Figure 8-2. | Comparison of Monthly Sewer Rates Associated with Initial Project Sequence Alternatives and the No Action Alternative (with Inflation) .............................................. 8-5 |
| Figure 8-3. | Comparison of Amount Added to Monthly Sewer Rates (No Action Alternative) by the Initial Project Sequence Alternatives (with Inflation) .................................................. 8-7 |
| Figure 8-4. | WTD-Recommended Project Sequence with 2030, 2035, and 2040 Long-term CSO Control Plan Completion Dates .......................................................................................... 8-8 |
| Figure 8-5. | Comparison of Annual Capital Expenditures for 2030, 2035, and 2040 Long-term CSO Control Plan Completion Dates for WTD-Recommended Project Sequence (2010 Dollars) ..................................................................................................................... 8-9 |
| Figure 8-6. | Comparison of Monthly Sewer Rates for 2030, 2035, and 2040 Alternative Long- term CSO Control Plan Schedules with WTD-Recommended Project Sequence and No Action Alternative (with Inflation) ............................................................................. 8-11 |
| Figure 8-7. | King County Executive’s Recommended Project Sequence and Schedule ...................... 8-13 |
| Figure 8-8. | Distribution of the Poverty Rate by Census Blocks in King County Service Area .......... 8-19 |
| Figure 8-9. | Median Household Income by 2000 Census Block Group in King County Service Area .................................................................................................................................. 8-23 |
| Figure 10-1. | King County Executive’s Recommended Project Sequence and Schedule ...................... 10-2 |

List of Tables

Table ES-1.   King County Executive’s Recommended CSO Control Plan ......................................... ES-13 Table 1-1.   2011 King County CSO Control Status ................................................................................ 1-14

Table 1-2.   Uncontrolled CSO Sites and Facilities in King County ....................................................... 1-19 Table 1-3.   WAC 173-245-040(2) Requirements for CSO Control Plan Update ................................... 1-20 Table 1-4.   EPA CSO Control Policy Requirements for Long-term Control Plan ................................. 1-23 Table 2-1.   Adopted Alternatives in Order of Priority .............................................................................. 2-4 Table 3-1.   CSO Control Projects Completed or Underway ................................................................... 3-13 Table 3-2.   Associated Projects with CSO Control Benefits Completed or Underway .......................... 3-15

Table 3-3.   Annual Average Frequency and Volume of Untreated CSOs:  Monitored CSOs

Compared to Modeled CSOs ............................................................................................ 3-17 Table 4-1.   RWSP and 2003 Updated Population Forecasts (2000 to 2050) ............................................ 4-8 Table 4-2.   RWSP and 2003 Updated Flow Projections (2000 to 2050) .................................................. 4-9 Table 4-3.   West Point Influent Loading Rates from Flow and Waste Load Study ................................ 4-11 Table 4-4.   CSO Treatment at West Point Treatment Plant .................................................................... 4-12 Table 4-5.   Key Results from October 2010 Modeling Run ................................................................... 4-14 Table 4-6.   Summary of Sensitive Area Rankings .................................................................................. 4-27 Table 4-8.   CSO Control Area Priority Based on Evaluation of Environmental Priorities ..................... 4-28 Table 5-1.   Feasibility Assessment for CSO Control Approaches ............................................................ 5-5 Table 5-2.   Final Alternatives Evaluated for This Review ...................................................................... 5-11

Table 5-3.   Triple-Bottom-Line Analysis of Site Alternatives for Ship Canal—11th Ave NW,

3rd Ave W, University, and Montlake ............................................................................. 5-22

Table 5-4.   Triple-Bottom-Line Analysis of Area Alternatives for Ship Canal—11th Ave NW,

3rd Ave W, University, and Montlake ............................................................................. 5-23

Table 5-5.   Triple-Bottom-Line Analysis of Area Alternatives for Middle EBI—Hanford #2,

Lander St, Kingdome, and King St .................................................................................. 5-27

Table 5-6.   Triple-Bottom-Line Analysis of Site/Area Alternatives for Middle EBI—Hanford #1 ....... 5-29 Table 5-7.   Triple-Bottom-Line Analysis of Site Alternatives for South EBI ........................................ 5-30 Table 5-8.   Triple-Bottom-Line Analysis of Area Alternatives for South EBI ....................................... 5-32

Table 5-9.   Triple-Bottom-Line Analysis of Area Alternatives for West Duwamish—W Michigan St

and Terminal 115 .............................................................................................................. 5-33

Table 5-10.  Triple-Bottom-Line Analysis of Site/Area Alternatives for West Duwamish—

Chelan Ave ....................................................................................................................... 5-34

Table 5-11.  Summary of CSO Basins not Recommended for GSI ......................................................... 5-37 Table 5-12.  GSI Alternative Summary Table ......................................................................................... 5-41 Table 6-1.   Summary of Costs for Recommended Preferred Alternatives ................................................ 6-3

Table 7-1.   Ability of Project Sequence Alternatives to Meet Schedule Drivers ...................................... 7-7 Table 8-1.   CSO Control Projects Now Under Way ................................................................................. 8-2

Table 8-2.   Comparison of Monthly Sewer Rates with Initial Project Sequence Alternatives and the

Increase over the No Action Alternative (with Inflation) ................................................... 8-6

Table 8-3.   Comparison of Amount Added to Monthly Sewer Rate by the Project Sequences

(2015−2030, with Inflation) ............................................................................................... 8-6

Table 8-4.   Comparison of Monthly Sewer Rates with 2030, 2035, and 2040 Alternative CSO

Control Program Schedules and Increase over the No Action Alternative

(2015−2040) ..................................................................................................................... 8-12

Table 8-5.   Estimates of Future Annual Sewer Rates with and without King County Executive’s

Recommended CSO Control Plan .................................................................................... 8-17

Table 8-6.   King County Annual Income Distribution, 2010 ................................................................. 8-22

Table 8-7.   Comparison of Results of Phase 1 Strict Adherence to EPA Guidance Methodology to

Phase 2 Supplemental Information ................................................................................... 8-24 Table 10-1.   King County Executive’s Recommended CSO Control Plan ............................................. 10-3

Appendices

Appendix A. CSO Control Planning Assumptions, Policies, and Implementation

Appendix B. Hydraulic Modeling and Monitoring Protocols, Model History

Appendix C. Change Matrix from 1999 Plan Amendment: Summary of Review for Change in  Uncontrolled CSO Basins

Appendix D. West Point Treatment Plant Flow and Waste Load Report Summary

Appendix E. Environmental Characterization and Prioritization

Appendix F. Summary of 2010-11 Public Involvement Activities

Appendix G. Rate Forecasting and Affordability

Appendix H. Post-Construction Monitoring Plan

Acronyms

| AACE | Association for the Advancement of Cost Engineering |
| --- | --- |
| AKART | all known available and reasonable technologies |
| AWWF | average wet-weather flow |
| BAT | best available technology economically achievable |
| BCT | best conventional pollutant control technology |
| BMP | best management practice |
| BOD | biochemical oxygen demand |
| CATAD | computer augmented treatment and disposal |
| CEPT | chemically enhanced primary treatment |
| CERCLA | Comprehensive Environmental Response, Compensation and Liability Act |
| CIP | Capital Improvement Program |
| City | City of Seattle |
| County | King County |
| CSL | Cleanup Screening Level |
| CSO | combined sewer overflow |
| CSOCP | combined sewer overflow control policies |
| CSS | combined sewer system |
| CWA | Clean Water Act |
| DDT | dichlorodiphenyltrichloroethane |
| DO | dissolved oxygen |
| DNR | Washington State Department of Natural Resources |
| DSN | Discharge Serial Number |
| EBDRP | Elliott Bay/Duwamish Restoration Program |
| EBI | Elliott Bay Interceptor |
| Ecology | Washington State Department of Ecology |
| EPA | U.S. Environmental Protection Agency |
| ESA | Endangered Species Act |
| FOG | fats, oil, and grease |
| gpad | gallons per acre-day |
| gpd | gallons per day |
| GIS | Geographic Information Systems |
| GSI | green stormwater infrastructure |
| HPA | Hydraulic Permit Approval |
| I/I | infiltration and inflow |
| LDW | Lower Duwamish Waterway |
| LTA | long-term-average |
| LTCP | long-term control plan |
| Metro | Municipality of Metropolitan Seattle |
| MG | million gallons |
| MGD | million gallons per day |
| MHI | median household income |
| MTCA | Model Toxics Control Act |
| NEPA | National Environmental Policy Act |
| NOAA | National Oceanic and Atmospheric Administration |
| NPDES | National Pollutant Discharge Elimination System |
| NSA | Northern Service Area |
| O&M | operations and maintenance |
| ORP | oxygen reduction potential |
| PAHs | polycyclic aromatic hydrocarbons |
| PBDEs | polybrominated diphenyl ethers |

| PCBs | polychlorinated biphenyls |
| --- | --- |
| PCEP | Puget Sound Estuary Program |
| PFD | Public Facilities District |
| PLCs | programmable logic controllers |
| PSRC | Puget Sound Regional Council |
| QA/QC | quality assurance/quality control |
| RCE | Residential Customer Equivalent |
| RCW | Revised Code of Washington |
| RI/FS | remedial investigation and feasibility study |
| RWQC | Regional Water Quality Committee |
| RWSP | Regional Wastewater Services Plan |
| SACE | Seattle Area Combined Sewer Overflow Evaluator |
| SACRO | Seattle Area Central Routing Organization |
| SAP | sampling and analysis plan |
| SCADA | Supervisory Control and Data Acquisition |
| SD | storm drain |
| SDOT | Seattle Department of Transportation |
| SEPA | State Environmental Policy Act |
| SMP | Sediment Management Program |
| SMS | Sediment Management Standards |
| SPU | Seattle Public Utilities |
| SQGs | Sediment Quality Guidelines |
| SQS | sediment quality standards |
| SR | State Route |
| SSA | Southern Service Area |
| SSACRO | South Seattle Area Control Routing Organization |
| TBL | triple bottom line |
| TBT | tributyl tin |
| TM | Technical Memorandum |
| TMDL | Total Maximum Daily Load |
| TOC | total organic carbon |
| TPP | Treatment Plant Policy |
| TSS | total suspended solids |
| USFWS | United States Fish and Wildlife Service |
| WAC | Washington Administration Code |
| WQA | water quality assessment |
| WQS | Water Quality Standards |
| WRIA | Water Resource Inventory Area |
| WSDOT | Washington State Department of Transportation |
| WTD | Wastewater Treatment Division |
| WWSP | wastewater services policies |

Executive Summary

This 2012 Combined Sewer Overflow (CSO) Control Program Review Report is a companion to the King County Executive’s Recommended CSO Control Plan. This report documents the County’s review of its CSO Control Program, which was conducted in accordance with policies and guidelines in the 1999 Regional Wastewater Services Plan (RWSP). It is supported by technical memorandums that can be found at http://www.kingcounty.gov/environment/wastewater/CSO/ProgramReview/plan.aspx#techmemos.

These reports, the supporting technical memorandums, and legislation are being transmitted on June 15, 2012 from the King County Executive to the King County Council for adoption of the recommended amendments to the County’s Long-term CSO Control Plan (Plan). The County’s Plan was last amended in 1999. Adoption is anticipated by fall of 2012. This transmittal and adoption of the King County Executive’s Recommended CSO Control Plan, which includes a 2030 Plan completion date, are intended to meet the requirements of a 2011 Washington State Department of Ecology (Ecology) administrative order.

Report Purpose

King County issues CSO Control Program reviews and updates or amendments to the County’s Long-term CSO Control Plan (Plan) approximately every five years to support county decisionmaking and renewal of the National Pollutant Discharge Elimination System (NPDES) permit for the West Point Treatment Plant. Adopted changes to the County’s Plan will be incorporated into the 2012 Long-term CSO Control Plan Amendment to be submitted to Ecology and the United States Environmental Protection Agency (EPA) in fall of 2012. This process is presented in Figure ES-1. This 2012 CSO Control Program Review Report documents the County’s most recent review of its CSO Control Program.

Figure ES-1. King County 2012 Long-term CSO Control Plan Amendment Process

Background

CSOs are untreated discharges of wastewater and stormwater into water bodies during heavy rainfall events when combined sewers are full. Combined sewers, which carry both wastewater and stormwater, exist in many parts of older cities across the nation, including the City of Seattle. Stormwater can cause extreme variations in wastewater flows, resulting in the need for large wastewater facilities and in challenges to the treatment process. To avoid sewer backups into homes, businesses, and streets during heavy rainfall events, combined sewers in the City of

Seattle sometimes overflow into Puget Sound, the Duwamish Waterway, Elliott Bay, Lake Union, the Lake Washington Ship Canal, and Lake Washington. Within the King County wastewater service area, CSOs only exist within the City of Seattle. Based on agreements made at the start of the regional system in 1958, both the County and City of Seattle are responsible for CSOs and are working to control them under long-term CSO control plans. Figure ES-2 shows the locations of the County’s and City of Seattle’s CSOs.

Although the wastewater in CSOs is greatly diluted by stormwater, CSOs may be harmful to public health and aquatic life because they can carry chemicals and disease-causing pathogens. CSO control protects public health and the environment by accomplishing the following:

- Reducing the potential for contact with pathogens and consumption of contaminated fish

- Reducing the potential for chemical exposure to salmon at their most vulnerable life stage

- Contributing to efforts to restore and protect Puget Sound

- Helping to meet the Duwamish Waterway long-term cleanup goals by reducing the volume of CSOs.

Figure ES-2. King County and City of Seattle CSO Locations

The County’s Long-term CSO Control Plan (Plan), implemented through the County’s CSO Control Program, outlines measures for controlling CSO discharges to surface waters, including controlling pollution at its sources, optimizing flow management, monitoring and modeling flows in the system, and constructing CSO control facilities. The Plan was last amended in 1999 (1999 Plan Amendment) as a component of the County’s RWSP. The 1999 Plan Amendment outlines measures for controlling CSOs to comply with federal and state water quality requirements. Ecology requires control of each CSO such that an average of one untreated discharge may occur per year. CSO sites that meet this requirement are classified as “controlled.” Those that do not are called “uncontrolled” CSO sites.

Construction of CSO control facilities in the region began in the late 1970s. Thus far, approximately $389 million has been spent to reduce untreated wastewater and CSO volumes from over 2 billion gallons per year in 1980 to 800 million gallons per year (see Figure ES-3).

Today, 16 of the County’s 38 CSO sites are controlled to Ecology’s standard; 14 CSO sites remain uncontrolled and are the subject of this review. In addition, the County currently has five CSO control projects underway, and three CSO sites are being refined and adjusted to meet the control standard.

Uncontrolled King County CSO Sites

The 14 uncontrolled CSO sites discharge CSOs to Elliott Bay, the Duwamish River (Lower,

East, and West Waterways), and the Lake Washington Ship Canal (including the Montlake Cut).

Figure ES-3. Historical Reduction in Volumes Since

Construction of the Regional System (1958-79) and CSO Control (1979-Present)

These CSO sites were grouped into areas for evaluation (see Figure ES-4), so that alternatives could be combined to provide control of all uncontrolled CSO sites in a given area:

- Ship Canal – 11th Ave NW, 3rd Ave W, University, and Montlake

- Middle Elliott Bay Interceptor (EBI) – Hanford #2, Lander St, Kingdome, and King St

- Middle EBI – Hanford #1

- South EBI – S Michigan St and Brandon St

- West Duwamish – W Michigan St and Terminal 115

- West Duwamish – Chelan Ave

Figure ES-4. King County CSO Site and Program Review Areas

CSO Control Program Review Approach

To conduct this most recent review, King County staff gathered and assessed information generated since adoption of the 1999 Plan Amendment. This review identified CSO control alternatives for each of the County’s 14 uncontrolled CSO sites and developed an implementation schedule and rate/capacity charge analysis for the recommended preferred alternatives. This review also identified conditions and actions to optimize CSO control facilities that have already been built but for which adjustments are still needed to achieve full control.

This review considered changes in conditions that could impact the type, size, location, sequence, or schedule for the 1999 Plan Amendment adopted alternatives. Changes considered include regulatory and policy changes, new technologies, existing CSO control performance, human and environmental health priorities, hydraulic modeling of the County’s combined sewer system, green stormwater infrastructure (GSI) opportunities, site availability, public opinion, and coordination with the City of Seattle and other agencies.

Alternative Evaluation Methodology

The following methodology was used in this review to update the CSO control recommendations from the 1999 Plan Amendment for the 14 uncontrolled CSO sites:

- An initial assessment identified CSO control approaches that are feasible for each uncontrolled CSO site. These are described in Chapter 5 of this report and Technical Memorandum 970, CSO Control Alternatives Development.

- A set of preliminary alternatives was developed from two sources:

  - The 1999 Plan Amendment adopted alternatives

  - New project alternatives developed by using the identified feasible CSO control approaches, new modeling results, changes in available siting, newly identified potential for GSI approaches, or newly identified potential for coordination with the City of Seattle.

- New joint project alternatives were developed and evaluated that would control both King County and City of Seattle CSO discharges where project costs and community impacts might be reduced.

- The preliminary alternatives were screened based on technical considerations, relative cost-effectiveness, community and public health, environmental impacts, land use and permitting, and operation and maintenance implications.

- Preliminary alternatives that were not screened out were further developed into final alternatives by refining the cost, size, and location of the alternatives. A triple-bottomline analysis of the final alternatives was performed to identify recommended preferred alternatives.

- GSI (or green) alternatives were developed and evaluated in parallel with final conveyance, storage, or treatment alternatives (also referred to as gray alternatives) for uncontrolled CSO basins with potential for GSI retrofit. Runoff volume reduction benefits and planning-level life-cycle costs were estimated. The GSI alternatives deemed cost-effective were identified with the recommended preferred alternatives. The sizes of the gray alternatives were conservatively not reduced to account for the GSI benefit in this review. Future evaluations, including enhanced monitoring and modeling, will quantify and then verify the benefit of GSI techniques prior to gray facility sizing.

- Recommended preferred alternatives were carried forward into the sequence and rate/capacity charge analysis.

Recommended Preferred Alternatives

Table ES-1 presents the recommended preferred alternatives for controlling King County’s remaining 14 uncontrolled CSO sites and estimated project cost. Potential GSI alternatives are also described in this table; however, the potential reduction in CSO control volume or CSO peak flow rate that could be achieved by implementing GSI in the CSO basin is not reflected in the costs or sizes of the proposed traditional CSO control facilities (gray facilities). It is anticipated that GSI costs will replace or reduce costs in these estimates. The $711-million-cost projection for the recommended Plan is based on project costs at a planning level of detail. As projects are designed, the costs of the project will be better understood. The general cost of construction will also vary over time depending on conditions at the time projects are bid; however, the County will diligently seek cost efficiencies.

Schedule, Rate Forecasting, and Affordability

This review included an evaluation of project sequence alternatives for implementing the recommended preferred alternatives, as well as schedules with three completion dates (2030, 2035, and 2040). Rate analysis indicated that the sewer rates did not differentiate between alternatives. The project sequence alternatives were then evaluated against the schedule drivers:  the ability to complete GSI effectiveness monitoring, prioritizing Duwamish area projects to coordinate with the river cleanup, and coordination with City of Seattle schedules and other agencies’ projects. As a result, a hybrid project sequence was developed and recommended that prioritizes the Duwamish coordination and GSI implementation. The WTD-recommended project sequence is presented in Chapter 7 of this report and Technical Memorandum 1100, Project Sequence.

A rate impact analysis compared schedules for completing the 2011 WTD Recommended CSO Control Plan of 2030, 2035, and 2040, and a No Action Alternative, which assumes no future control projects beyond projects now underway (Puget Sound Beach projects plus the CSO control component of the Ballard Siphon Replacement project.) The rate impact analysis indicated that all the alternative schedules for completing the Plan result in approximately the same level of rate increase, with the extended schedules ending slightly higher than the 2030 schedule but having a slower rate of increase in the earlier years of the schedule. These differences were not considered sufficient reason to change the 2030 completion date.

Continuation of the 2030 schedule, as adopted in the 1999 Plan Amendment, was recommended. Under the 2030 schedule, the monthly sewer rate impacts will increase by $7.61 per month (estimated with inflation) due to implementing the Plan by 2030.

To have a better understanding of the impact of implementing the recommended Plan, the County conducted a two-phased analysis of financial capability and affordability. Phase 1 strictly followed guidelines established by EPA, and Phase 2 followed EPA guidelines but included supplemental information to better understand the regional diversity of households. More detail about the financial capability and affordability analysis is provided in Chapter 8.

As highlighted over the past several years, downturns in the economy can happen quickly. Indicators used in the financial capability and affordability analysis, such as median household income and poverty, have all been adversely affected over the past three to five years. The County needs to track these indicators to regularly evaluate the financial capability to implement the recommended Plan and the ability of the ratepayers to pay for the Plan over time.

As part of the required CSO control program reviews completed ahead of the NPDES updates of the Plan, which occur approximately every 5 years, the County will reevaluate the affordability indicators and routinely evaluate financial capability and affordability of the Plan. This will insure that there is a discussion of the ratepayers’ ability to pay for the Plan and that the County does not overburden its own finances or those of the community it serves.

Public Review and the King County Executive’s Recommended CSO Control Plan

The 2011 WTD Recommended CSO Control Plan was released for public comment in October 2011. Copies of the formal comment letters are presented in Appendix F of this report. Based on input received, including concerns raised by some members of the public about whether dollars spent on CSO control is the best investment in water quality, the King County Executive recommends the following:

- Moving forward with nine CSO control projects to control the remaining 14 uncontrolled CSO sites by 2030. Their estimated project cost is $711 million (2010 dollars). The nine projects are the same as those described in the 2011 WTD Recommended CSO Control Plan.

- Conducting a water quality assessment and monitoring study (study) to inform the next CSO control program review for the 2019 NPDES permit renewal. The Executive believes it is prudent to meet the County’s CSO control commitments and also commit resources into completing a comprehensive review of the effects on water quality in the sub-watersheds where CSO discharges occur. Study results could confirm or propose adjustments to the County’s Long-term CSO Control Plan to meet water quality standards and ensure that actions by the County and other entities improve water quality, health, and biological outcomes that are well integrated and sequenced to provide the greatest benefit in each CSO discharge watershed. Ecology and EPA will need to review and approve any changes to the Plan that result from the study recommendations.

- Implementing the first projects in the Plan—Hanford #1 and S Michigan St/Brandon St— now. However, the next two projects—3rd Ave W and Chelan Ave—will start in 2017, two years later than stated in the 2011 WTD Recommended CSO Control Plan, to enable study findings and recommendations to confirm or adjust control priorities. Unless changes are recommended in the next Program Review, the CSO control projects recommended in the Plan will be completed by 2030. The Plan continues the commitment to implement Lower Duwamish Waterway projects in coordination with river cleanup, to implement GSI in four CSO basins, and to pursue three joint projects with the City of Seattle. Figure ES-5 shows the sequence and schedule of recommended projects as adjusted to accommodate the water quality assessment and monitoring study.

Figure ES-5. Project Sequence and Schedule in King County Executive’s Recommended CSO Control Plan

King County Council Review and Long-term CSO Control Plan Amendment Adoption

This 2012 CSO Control Program Review Report and the King County Executive’s

Recommended CSO Control Plan are being submitted to the King County Council and the public in June 2012. It is expected that the Council will refer the Plan to the Regional Water Quality Committee (RWQC) for initial review and deliberations. The public will be able to comment and provide testimony on the Plan as part of the King County Council’s deliberations. Information on how to provide input will be available on the CSO Control Program website at: http://www.kingcounty.gov/csoreview.

The RWQC may recommend changes to the Plan and CSO control policies. The amended Plan is expected to be adopted by the King County Council in fall of 2012. After the King County Council adopts the amended Plan, the County’s 2012 Long-term CSO Control Plan Amendment will be finalized and submitted to Ecology and EPA in the fall of 2012. Implementation of projects contained in the adopted Plan will begin immediately.

“Alternative” refers to a planning-level project concept.

A triple-bottom-line analysis evaluates environmental and social, in addition to financial metrics. This analysis is described in this report and Technical Memorandum 970, CSO Control Alternatives Development.

The design status of the alternatives in the recommended Plan is such that the cost estimates are Association for the Advancement of Cost Engineering (AACE) Class 5 estimates. The accuracy range for Class 5 estimates is –50 percent to +100 percent. See Technical Memorandum 620, Cost Estimating Methodology for CSO Control Facilities for details.