| # UTRC Review of the Ames Lake Water Association 2008 Water System Plan |  |  |
| --- | --- | --- |
| A review of the specific statutes, rules, codes, and polices to the Association’s plan is as follows: |  |  |
|  | A. General and water and sewer plan: King County Code 13.24.010; 13.28 | Comments/findings |
| (1) | - Review is applicable to water utilities distributing or obtaining water in unincorporated King County, and/or utilities that distribute water within a Critical Water Supply Service Area (ch. 70.116 RCW). - Is there a need to meet the consistency requirements of RCW 43.20.260? | - Yes, the Ames Lake Water Association’s (Association) comprehensive water plan (Plan) is subject to King County Council approval under Ch. 70.116 RCW and King County Code (KCC). The Association provides water service to a part of eastern unincorporated King County. - Yes, the Association also needs to demonstrate consistency for its Plan under RCW 43.20.260. |
| (2) | - Consistency with King County Comprehensive Plan and Development regulations, and policies including KCC 21A.28.040 development standards, provision of adequate supplies for anticipated growth and development. | - Yes, the Association’s Plan is consistent. |
| (3) | - Infrastructure for existing and future service areas based on adopted land use map. | - Yes. The Association’s service area is located entirely in unincorporated King County. The King County land use map is used in the Plan. |
| (4) | - Review proposals for modified or expanded service areas based on compliance with utility’s approved plan, and ability to meet duty to serve requirement. | - Not applicable. The Association’s service area is well defined and is bounded on several sides by other water utilities. The service area has not changed recently and the Association does not expect it to change. |
| (5) | - Sufficient information to demonstrate the ability to provide service consistent with the requirements of all applicable statutes, codes, rules, and regulations. | - Yes, the Plan demonstrates the Association’s ability to provide service consistent with applicable statutes, codes and regulations. The Association obtains its water from seven wells located in two well fields. The projected daily demand in 2033 is approximately 529,900 gallons per day (gpd) without conservation and 408,900 gpd with conservation. The Association is currently projecting a shortfall in supply to occur as early as 2012, but is working on ways to remedy it. |

| (6) | - Monitor and review effectiveness of purveyor conservation plans if within area covered by an approved Coordinated Water System Plan (CWSP). | - The Association is in the area covered by the East King County CWSP. - Through its membership in the East King County Regional Water Association the Association participates in the Partnership for Water Conservation. The Association’s water use efficiency plan is organized to conform to the requirements of the Water Use Efficiency Rule. |
| --- | --- | --- |
|  | B. Consistency requirements: 13.24.060 |  |
| (7) | - State and local health requirements. | - Yes. |
| (8) | - Creation and maintenance of logical service areas. | - Yes, the service area is logical. - The Association’s boundaries are fairly well fixed and not expected to change, with other utilities abutting the Association on several sides. |
| (9) | - Elimination or prevention of duplicate facilities. | - Yes. The Association intends to provide service within its service area by means of direct connection. The Association does not foresee any need to provide satellite management services, since direct service is available throughout its service area. - The Association currently has no interties, but it is looking into entering into an agreement with Sammamish Plateau Water and Sewer that would provide emergency supplies as well as allow the wheeling of water from Seattle Public Utilities (SPU). |
| (10) | - Promotion of most healthful and reliable services to the public. | - Yes. A hydraulic analysis performed for the Association shows that the Association has pressure problems. The Association’s capital improvement plan (CIP) is focused on remedying those problems. - The hydraulic analysis of the Association’s system identifies improvements that need to be made to the distribution system, particularly the installation of booster pumps and pressure reducing valves to improve pressure and supply conditions. The CIP addresses those needs. - The Association will need additional water supplies to meet peak day and peak hour demand through the six- and 20-year planning periods. The Association is investigating several options, including redeveloping existing wells or drilling new ones, activating emergency wells, or obtaining water from SPU. - Water purveyed by the Association complies with public health standards. |
| (11) | - Provision of service at a reasonable cost, and maximization of use of public facilities. | - Yes, the Association’s rates for water service are comparable to the rates charged by similar utilities. The Association raised its rates in 2007 and expects to do so again in 2012 to bring revenues in line with operating costs and the cost of implementing the CIP. - The Association has adopted a graduated rate structure to encourage efficiency of water use. |
| (12) | - King County Comprehensive Plan and other pertinent county adopted plans and policies. | - Yes, there is consistency between the Association’s Plan and the King County Comprehensive Plan. |
| (13) | - Basin-wide or multibasin water plans, sewerage plans, or both when approved by the Washington State Department of Ecology (Ecology) or Washington State Department of Health (DOH). | - The Association has not been involved in multibasin water plans, although it is an associate member of the East King County Regional Water Association. - The Association neither collects nor treats wastewater. |
| (14) | - Applicable state water quality, water conservation, and waste management standards. | - Yes, applicable standards are met. The Association tests water from all its wells in accordance with DOH protocols. - The Association’s water use per equivalent residential unit (ERU) in 2007 was 192 gpd, not accounting for distribution system losses. The Association is calculating maximum day demand at 2.25 times average day demand. The Association’s conservation activities should reduce the peaking numbers. - The Association’s distribution system loss (non-revenue or unaccounted-for water) has fluctuated between 1.4 and 8.2 percent in recent years (the 1.4 percent reading may have been too low due to a faulty meter). The Association is committed to staying below the ten percent standard in the Water Use Efficiency Rule. - The Association successfully participated in the East King County Regional Water Association’s regional effort to achieve eight percent reduction in water use by 2000. The Association’s main means for achieving conservation is through rates, which produced significant water savings when they were last increased in 2007. |

| (15) | - Water Resources Act (RCW 90.54). | - The Association has had a conservation program in place since 1990. The Association’s Water Use Efficiency Plan is organized to conform to the requirements of the Water Use Efficiency Rule adopted by DOH. The Plan makes no connection between the Association’s conservation program and the requirements of RCWs 90.54.180 and 90.03.386. |
| --- | --- | --- |
| (16) | - Growth Management Act (GMA) (RCW 36.70A). | - The Association used Puget Sound Regional Council data in preparing its forecasts. The Growth Management Planning Council data for unincorporated King County show less growth. - The six-year portion of the CIP identifies public money the Association may need for capital facilities. |
| (17) | - Ground water management plans. | - The Association participated in the development of the East King County Ground Water Management Plan. |
| (18) | - Federally approved habitat conservation plans and recovery plans under the Endangered Species Act (ESA). | - Not applicable. |
| (19) | - Requirements for salmon recovery under Ch. 77.85 RCW, and other plans, including regional water supply or water resource management plans. | - Not applicable. |
| (20) | - Applicable requirements to evaluate opportunities for the use of reclaimed water under chapter 90.46 RCW and CO-7. | - The Plan includes a brief evaluation of opportunities for the use of reclaimed water as required by chapter 90.46 RCW. Those opportunities are limited due to the fact that all waste treatment within the Association’s service area is by means of on-site septic systems. |
|  | C. King County Comprehensive Plan—consistency with provisions and specific policies (Water System Plan) |  |
|  | COUNTYWIDE PLANNING POLICIES |  |
| (21) | FW-5: management of resources for multiple beneficial uses, including flood and erosion hazard reduction. | - Not applicable. |
| (22) | FW-12(c): ensure sufficient water supply for growth and fish habitat needs through long-term planning. | - Not at present. The Association is forecasting a near-term shortfall in water supplies but is investigating the means to address it. There is no apparent linkage and little relevance of the Plan to fish habitat needs. |
| (23) | CA-5, CA-6, and E-434 and policies to protect quantity and quality of ground water. | - The Association complies with DOH requirements for the testing of its ground water supplies. The Association also has wellhead protection programs for all of its wells. |
| (24) | CO-5: water supply shall be regionally coordinated. | - Yes, the Association’s supply is regionally coordinated through its membership in the East King County Regional Water Association. The Association is also pursuing establishment of an intertie with the Sammamish Plateau Water and Sewer District for emergency supplies. |
| (25) | CO-6: aggressive conservation efforts shall be implemented. | - The Association has organized its conservation program to conform to the requirements of the water use efficiency program rule adopted by DOH. The Association also participates in East King County Regional Water Association conservation programs. |
|  | KING COUNTY COMPREHENSIVE PLAN POLICIES |  |
| (26) | F-102: King County will provide or manage countywide services, which include wastewater, water resource management, surface water management, flood warning and floodplain management, protection and preservation of natural resource lands. | - Yes, since the Association’s service area is entirely within unincorporated King County. |
| (27) | F-104: plan for provision of services to rural areas. | - Yes, since the Association provides water to unincorporated King County. |
| (28) | F-105: King County to work with cities and service providers to establish priority areas for public funding of capital facilities. | - The capital facilities plan is adequate and appropriately focused. |
| (29) | F-201: all facilities and services should be provided in compliance with provisions and requirements of the ESA. | - Yes. |
| (30) | F-202: ensure adequate supply of public facilities to support communities. | - Yes, although the Association is facing a near-term shortfall in water supplies, it is looking to secure additional supplies, and has an arrangement for emergency supply from an adjacent utility. |
| (31) | F-203: King County will work with cities, special purpose districts, and other service providers to define regional and local services and determine appropriate providers. | - Yes. |

| (32) | F-208: support rural levels of development and not facilitate urbanization. | - The Association’s service area is entirely outside the UGA and the Association projects that future development will be essentially rural in nature. |
| --- | --- | --- |
| (33) | F-209 and F-212: capital facility plans and improvement programs for services to unincorporated King County are consistent with King County Comprehensive Plan. | - Yes, the capital facility plan is consistent with the King County Comprehensive Plan. |
| (34) | F-210: King County helps coordinate development of utility facilities. | - Yes, to the extent applicable, King County will do this. |
| (35) | F-215: King County shall initiate a sub-area planning process with any service provider that declares, in its capital facilities plan, an inability to meet service needs within service area. | - The Association did not identify any inability to meet service needs within its service area at present. |
| (36) | F-217: where an area-wide sewer, water, or transportation deficiency is identified, King County and applicable service providers shall remedy the deficiency through a joint planning process. | - No area-wide water deficiency is identified. The Association is addressing its projected shortfall. At this point, there is no need for King County’s involvement in solving this problem. |
| (37) | F-225: King County supports coordination of regional water supply planning, sales of excess water among municipalities, water quality programs, and water conservation and reuse programs. | - The Association is pursuing an agreement with the Sammamish Plateau Water and Sewer District for an intertie to provide emergency water supplies. The Association is also a member of the East King County Regional Water Association. |
| (38) | F-226: group A water systems must meet duty to serve requirement within service area as defined under CWSP or by individual water system plans. | - Yes, the Association is committed to meeting its duty to serve. Also see comments 4 and 5. |
| (39) | F-227-231: provides a hierarchy of water supply providers in unincorporated King County, depending on whether within UGA or rural areas, with preference for providing water from existing suppliers. | - The Association recognizes its duty to serve within its service area and is committed to providing water to all its customers within its service area by direct connection. Even though it can provide water by direct connection, the Association will consider providing satellite management services on a case-by-case basis. - There are no other Group A public water systems within the Association’s service area. |
| (40) | F-237: King County supports the use of interties consistent with planning, and implementation of approved ESA and Clean Water Act response requirements. | - The Association currently does not have any interties, but it is working on one with the Sammamish Plateau Water and Sewer District that could potentially be used to wheel SPU water. |
| (41) | F-239: King County partners with utilities to encourage best management practices and conservation through such means as developing reclaimed water, aggressive water conservation and reuse measures; support planned land uses with reliable service at minimum cost; encourage reclaimed water use, focused on large water users such as golf courses and cemeteries. | - King County is willing to work with the Association on these issues, particularly the evaluation of reclaimed water opportunities. |
| (42) | F-240: Utilities Technical Review Committee (UTRC) to consider (a) consistency with land use plans and development regulations; (b) approved or adopted plans for ground water, ESA, salmon recovery, water resources, watershed planning, regional water supply plan; and (c) the Regional Wastewater Services Plan. | - The UTRC did consider the given issues and recommends approval of the Plan. |
| (43) | F-241: in reviewing proposals for modified and expanded service area boundaries, the UTRC must include an evaluation of the utility’s compliance with its comprehensive water system plan, including water conservation elements, and whether it can meet its duty to provide service; no approval of service area where unable to provide service for reasons in RCW 43.20.260. | - The Association has no plans to extend its service area boundaries in the future. Given its supply problems, it makes sense that the Association does not consider expanding its service area for the time being. |
| (44) | F-243: public drinking water system reservoirs and watersheds should be managed primarily to protect drinking water supplies, but allow multiple uses when not jeopardizing water quality; downstream uses including recreation, fish, and agricultural resources. | - Not applicable. The Association’s storage facilities are tanks. |
| (45) | F-244: ground water supplies should be protected by preventing land uses that may adversely affect quantity or quality. | - The Association has a wellhead protection program to help protect its ground water supplies from detrimental land use practices. |