February 14, 2007

The Honorable Larry Gossett

Chair, King County Council

Room 1200

C O U R T H O U S E

Dear Councilmember Gossett:

Enclosed is an ordinance requesting supplemental appropriation of $7,000,000 to replace the North Mercer Island Pump Station Interceptor Line.  This line is located on both SE 24th Street and 84th Avenue SE as well as on Luther Burbank Park on Mercer Island.  On December 14, 2006 a powerful rain and windstorm caused outages and surges in the conveyance lines throughout King County resulting in damage to the interceptor referenced above.  The severity of this storm prompted me to issue a Local Proclamation of Emergency on December 15, 2006.  Further, Motion 12430, which was adopted by the King County Council on January 8, 2007, recognized the resultant damage of this storm and extended to March 1, 2007, the authority of the county to waive standard procurement processes to quickly mobilize to repair the damage.  This request for supplemental appropriation is to repair damage that resulted from the December 14, 2006 storm.

# How the problem was identified

The Wastewater Treatment Division (WTD) of the Department of Natural Resources and Parks was notified on December 20, 2006, by a citizen in the area, of a sinkhole, approximately 10 feet long, 2 feet wide, and 2 feet deep, on 84th Avenue SE on Mercer Island.  Further investigation and excavation revealed that an underground gravity sewer conveyance line made of a material called Techite had failed during the storm.  This pipe carries wastewater from residences in the area to the South Treatment Plant in Renton.  As soon as the damage was found, pumping within the line was lowered to relieve pressure on the damaged pipe.  A second sinkhole on the line developed approximately 10 feet upstream from the original sinkhole on December 21, 2006.  This was caused by a loss of backfill and gravel resulting from the original storm surge on December 14, 2006.  The enclosed map illustrates the pipe damage and bypass route.

# Initial response to emergency

WTD personnel inspecting the pipe determined that it would not hold for another significant event.  In response, it was decided to temporarily bypass the line in order to relieve stress on the pipe and initiate a permanent replacement of the pipe.  WTD, with construction support from Frank Coluccio Construction Company, installed an emergency bypass line that became operable on January 4, 2007.  An additional bypass of approximately 480 feet was completed January 18, 2007, running from just north of the lower entrance to Luther Burbank Park through the wetland to a private residence on the edge of the wetland.  The entire bypass consists of 18-inch high-density polyurethane pipe (HDPE), which is laid on top of the ground, with the exception of when it is lowered into the pavement and protected by steel sheets to allow driveway access.

# Current condition of pipeline at Mercer Island site

The county’s closed-circuit television (CCTV) crew sent a camera through the interceptor and located numerous fractures, in addition to the initial damaged area, within the Techite pipe.  The fractures were found in the pipe run of 950 feet along 84th Avenue SE.  A second run of 700 feet of pipe made of the same material on SE 24th Street was inspected with CCTV yielding no indication of factures along that run.  However, a third segment of the pipe, entering Luther Burbank Park from SE 26th Street, was found to have a 12-inch longitudinal fracture along the crown approximately 18 feet from the manhole through the parking lot to the wetland.  This additional fracture is problematic as it is unlikely to withstand high pressure surges from the newly installed bypass.  WTD has directed Coluccio Construction to bypass this last section of pipe so there will be no further risk of breakage or sewage spills in the area while a new pipe is installed.

All of the affected pipe is made of a reinforced fiberglass material called Techite, manufactured by Amoco.  The pipe, installed in 1966, was originally predicted to have a 50 year life span.  However, class-action level lawsuits cite failures occurring as early as seven years under less demanding uses such as irrigation.  The nature of Techite limits repair options because patching or other disturbances can result in damage to adjacent areas on the pipe which makes an acceptable repair extremely difficult to achieve.  At 40 years, the Techite pipe installed as part of the North Mercer Interceptor has provided 80 percent of predicted service life.

# Project approach

In light of the current condition of this pipeline, WTD staff is moving to replace the existing Techite pipe system from the pump station to the wetland with a new underground line made from HDPE on an emergency procurement basis pursuant to the authority granted in Motion 12430.  This action is based on two existing conditions: 1) the weakened state of the current pipeline system and 2) the inadvisability of using the above ground temporary bypass any longer than the minimum possible time as it is subject to possible damage or vandalism.

In this approach, the damaged pipe will be replaced by a pipe bursting technique that presents the least amount of disruption to the surface streets by allowing the old pipe to simply stay “in place” while new pipe is inserted and takes over the function.  This technique is widely used in trenchless pipe replacement.  If the soil composition within the wetland does not allow pipe bursting, traditional trenching methods will be used to replace the pipe segment.  Although structural issues or damage are not anticipated while working on the wetland arch, a separate $900,000 contingency budget is proposed to be used if necessary to protect a koi pond and landscaping located near the pipe bursting area.

# Schedule

The initial work on the replacement project began on January 19, 2007 once the final bypass pipe was installed.  Substantial completion of the replacement project, road and parking lot restoration, and demobilization will be accomplished by mid April 2007.  Wetland restoration will remain an open item until the fall when plantings will have the best opportunity to root and survive during the late fall and winter months.  Additionally, wetland monitoring will continue for at least another year post construction.

# Cost Estimate

The proposed budgetary breakdown for this project follows:

Installation of emergency bypass pipe		$375,000

Construction of Pipe Bursting Pits (8)		$600,000

Pipe Bursting, 2,450 Lineal Feet			$600,000

Road rebuild/restoration 				$1,200,000

Mitigation and Restoration at Wetland		$450,000

WTD Internal Staff					$500,000

Construction Services					$675,000

Allied Construction Costs				$700,000

Contingency

Risk Adjustments for Wetlands, Pipe Bursting	$900,000

General Project Contingency 			$1,000,000

Total Project Budget:						$7,000,000

As noted on the attached fiscal note, this project will be financed using bond proceeds.

Thank you for your consideration of this request.  If you have any questions, please contact Don Theiler, Division Director of the Wastewater Treatment Division in the Department of Natural Resources and Parks, at 206-684-1551.

Sincerely,

Ron Sims

King County Executive

Enclosures

cc:	King County Councilmembers

ATTN:  Ross Baker, Chief of Staff

Shelley Sutton, Policy Staff Director

Rebecha Cusack, Lead Analyst, Capital Budget Committee

Anne Noris, Clerk of the Council

Bob Cowan, Director, Office of Management and Budget (OMB)

Sid Bender, Budget Supervisor, OMB

Pam Bissonnette, Director, Department of Natural Resources and Parks (DNRP)

Don Theiler, Division Director, Wastewater Treatment Division (WTD), DNRP