| Review of The City of Pacific Comprehensive Water System Plan August 2017 |
| --- |
| Service Area The City of Pacific (City) owns and operates a water system located in southwestern King County with a part of the city located in northwest Pierce County. The area of the City is approximately 1,587 acres with 421 of these acres in Pierce County. The City borders include a small portion of unincorporated Pierce County to the southeast and to the southwest, the City of Sumner to the south, the City of Edgewood to the southwest, unincorporated King County to the west/northwest, the City of Algona to the north, and the City of Auburn to the north and northeast. There are five water systems adjacent to the City of Pacific water system; the adjacent water purveyors include the City of Auburn, City of Algona, City of Sumner, Lakehaven Utility District and the Mt. View – Edgewood Water Company. The City’s water system consists of one well field with three active wells, a 750,000-gallon reservoir, a 3,500 gallon per minute booster station, and approximately thirty miles of distribution pipe. The entire water system is a single pressure zone. Single-family residential land use is the predominant water use in the area, with considerable commercial and multi-family development over the past decade. The City of Pacific provides water to approximately 1,559 residential services, 106 multifamily accounts (serving approximately 838 units), 176 commercial accounts, and 26 supplemental accounts (e.g. irrigation). The City’s existing number of equivalent residential units (ERUs) in 2016 was 2,690 and is projected to be 4,030 ERUs in 2036. The City’s capital improvement plan recommends improvements totaling approximately $4.6 million dollars over the next six years. The City’s sources of revenue include rate revenues, existing reserves, connection charges, debt financing, grants, and developer contributions. Reclaimed Water The City did complete King County’s Water Reclamation Evaluation Checklist. Opportunities for use of reclaimed water are limited. SEPA The City completed a State Environmental Policy Act (SEPA) checklist for the Plan and, as lead agency under SEPA, issued a determination of nonsignificance for the approval of the Plan on February 24, 2017. There were no appeals. |
|  | A. General, water and sewer plan specific King County Code (KCC) 13.24.010 | Comments/findings |
| (1) | The code is applicable to water utilities that obtain water in unincorporated areas and provide service in unincorporated areas of King County. | The City provides water service within the area covered by the South King County Coordinated Water System Plan (CWSP). The City’s water service area includes areas inside and outside of the current City limits. The City’s Plan is subject to King County Council approval under Chapters 36.70A, 43.20 and 70.116 RCW. |
| (2) | Water system plans should be submitted every six years or sooner if required by the Washington State Department of Health (DOH). | The City’s last water plan was approved in 2011. The City submitted the Plan to the DOH in 2017 and will seek approval of the Plan. |
| (3) | The infrastructure for existing and future service areas based on adopted land use map. | Yes, King County land use and zoning maps were appropriately used in determining the water demand projections. |
| (4) | The Plan contains sufficient information to demonstrate the ability to provide services consistent with the requirements of all applicable statutes, codes, rules, and regulations. | Yes, the Plan demonstrates that the City has ample water supply to provide service consistent with the requirements of all applicable statutes, codes, rules, and regulations. |
| (5) | The Plan is consistent with Washington Administrative Code (WAC) 246-290-100 for the water service. | Yes, the Plan is consistent with the applicable rules. |
|  | B. Consistency requirements: 13.24.060 |  |
| (6) | King County Code related to the installation of fire hydrants and water mains. | Yes, the Plan proposes to provide adequate fire flow for the urban areas. |
| (7) | State and local health requirements. | The Plan has not yet been approved by DOH. The UTRC review process included a representative of Public Health-Seattle and King County. |
| (8) | Elimination or prevention of duplicate facilities. | The City has written agreements with other water providers regarding areas to be served in order to avoid overlapping jurisdiction and to ensure efficiency in the use of existing facilities. |
| (9) | Promotion of most healthful and reliable services to the public. | Yes. |
| (10) | Provision of service at a reasonable cost, and maximization of use of public facilities. | Currently, the City charges a rate that is in the affordable range. |
|  | C. King County Comprehensive Plan (KCCP) – consistency with provisions and specific policies |  |
| (11) | Consistency with the KCCP and applicable County plans and policies including the Flood Hazard Management Plan and Emergency Response Plan. | Yes, the Plan is consistent with the applicable comprehensive plans. |
| (12) | Consistency with the Coordinated Water System Plans adopted in KCC 13.28. | Yes, the Plan is consistent with the South King County Coordinated Water System Plan. Wherever feasible, the City may encourage satellite management as a part of its services within its service area. |
| (13) | Basin-wide or multi-basin water plans, sewerage plans, or both when approved by the Washington State Department of Ecology or the Washington State Department of Health. | Not applicable. |
| (14) | Applicable state water quality, water conservation (e.g., chapter 90.54 RCW and RCW 90.48.495), and waste management standards. | Yes. The City implements the minimum water conservation program. |
| (15) | Growth Management Act; chapter 36.70A RCW. | Yes, the Plan is consistent with the Growth Management Act. See specific policies below. |
| (16) | Groundwater Management Plans. | The City has updated its Wellhead Protection Program. The Wellhead Protection Areas have been or will be incorporated into the City and County critical aquifer recharge areas under the Growth Management Act. |
| (17) | Federally-approved habitat conservation plans and recovery plans under Endangered Species Act, and other plans, including regional water supply or water resource management plans. | The City is aware of, and supports, the planning done for the Puyallup-White River basin salmon recovery. There is no active applicable regional water supply plan. |
| (18) | Applicable requirements to evaluate opportunities for the use of reclaimed water under chapter 90.46 RCW. | Yes, the City evaluated reclaimed water use opportunities. |
| (19) | State Environmental Policy Act (SEPA) documentation. | The City completed a SEPA checklist and issued a determination of nonsignificance for approval of the plan on February 24, 2107, with no appeals. |
|  | COUNTYWIDE PLANNING POLICIES |  |
| (20) | DP‐13: All jurisdictions shall plan to accommodate housing and employment targets. This includes: “Coordinating water, sewer, transportation and other infrastructure plans and investments among agencies, including special purpose districts;…”. | Yes, the City does this. |
| (21) | PF‐4: Develop plans for long‐term water provision to support growth and to address the potential impacts of climate change on regional water resources. | The City obtains water supply from the ground. The Plan does not discuss climate change impacts on water supply. |
| (22) | PF‐5: Support efforts to ensure that all consumers have access to a safe, reliably maintained, and sustainable drinking water source that meets present and future needs. | Yes, the City does this. |
| (23) | PF‐6: Coordinate water supply among local jurisdictions, tribal governments, and water purveyors to provide reliable and cost‐effective sources of water for all users, including residents, businesses, fire districts, and aquatic species. | The City has agreements in place with neighboring systems for utility coordination. |
| (24) | PF‐7: Plan and locate water systems in the Rural Area that are appropriate for rural uses and densities and do not increase the development potential of the Rural Area. | Not applicable. |
| (25) | PF‐8: Recognize and support agreements with water purveyors in adjacent cities and counties to promote effective conveyance of water supplies and to secure adequate supplies for emergencies. | The City has agreements with neighboring utilities for emergency situations. |
| (26) | PF‐9: Implement water conservation and efficiency efforts to protect natural resources, reduce environmental impacts, and support a sustainable long‐term water supply to serve the growing population. | The District’s three-year average distribution system loss is nine percent which is below the action level of ten percent. |
| (27) | PF‐10: Encourage water reuse and reclamation, especially for high‐volume non‐potable water users such as parks, schools, and golf courses. | See 18. The City completed King County’s Water Reclamation Evaluation Checklist. There are no opportunities to use reclaimed water at this time. |
|  | KING COUNTY COMPREHENSIVE PLAN (KCCP) POLICIES |  |
| (28) | F-107: Plan for provision of services to rural areas. | Not applicable. |
| (29) | F-108: King County to work with cities and service providers to establish priority areas for public funding of capital facilities. | The capital improvement program (CIP) is adequate and appropriately focused with funding sources identified. |
| (30) | F-201: All facilities and services should be provided in compliance with provisions and requirements of the Endangered Species Act (ESA) and the Clean Water Act. | Yes, to the extent known, facilities and service are provided consistent with the federal laws. |
| (31) | F-209: Support rural levels of development and not facilitate urbanization. | Not applicable, as the City serves only the urban area. |
| (32) | F-210: Capital facility plans and improvement programs for services to unincorporated King County are consistent with the KCCP. | Yes, the CIP is consistent with the KCCP. |
| (33) | F-211: King County helps coordinate development of utility facilities. | Yes, to the extent applicable, King County will do this. |
| (34) | F-221: King County shall initiate a sub-area planning process with any service provider that declares, in its capital facilities plan, an inability to meet service needs within service area. | Not applicable. The City did not identify any inability to meet service needs within its service area. |
| (35) | F-223: If a service deficiency is identified in a service provider's existing service area, King County and the applicable service provider shall remedy the deficiency through a joint planning process addressing capital improvement programs and long-term funding strategies reuse programs. | Not applicable. The City did not identify any inability to meet service needs within its service area. |
| (36) | F-231: King County supports coordination of regional water supply planning, sales of excess water supplies among municipalities in the region, water quality programs and water conservation, reuse and reclaimed water programs. | Yes, the City supports regional water supply coordination. |
| (37) | F-232: Water utilities that obtain water from, or distribute water in unincorporated King County, and water utilities formed as special purpose districts under Title 57 RCW are required to submit water system plans to the County for review and approval and shall describe in their plans how they intend to meet their duty to provide service within their retail service areas. | The City distributes water outside the City limits and in unincorporated King County, so the plan is subject to review and approval by the King County Council. |
| (38) | F-248 King County shall partner with utilities to publicize water conservation and encourage best management practices that conserve potable water supply through measures that include use of alternative supplies such as reclaimed water. | Yes, the County does and will continue to do this. |
| (39) | F-246: King County supports interties that allow the transfer of water resources among water utilities to meet the projected demands for growth where such interties meet the requirements of RCW 90.03.383 and are also consistent with any applicable locally adopted comprehensive plans, regional water supply plans, adopted groundwater management plans, watershed plans, approved Coordinated Water System Plans, and response requirements of ESA and Clean Water Act. | The City has interties with the City of Auburn, the City of Algona, and the City of Sumner. All of the interties are for emergency use only and are manually operated. The Plan is consistent with the South King County Coordinated Water System Plan. |
| (40) | F-249: Utilities with more than one thousand service connections required to submit water system plans for approval to King County shall include an evaluation of reclaimed water use opportunities by completing King County’s Water Reclamation Evaluation. | The City did an evaluation of reclaimed water use. Reclaimed water use is not feasible at this time. |
| (41) | F-251: In its review of water system plans, the UTRC shall consider the criteria provided in KCC 13.24.010, 13.24.060, and 13.24.070, and determine the plan’s consistency with the following: a. Applicable provisions of the King County Comprehensive Plan, land use plans, and development regulations adopted under the Growth Management Act; b. Approved or adopted regional water resource plans, such as basin plans, groundwater plans, watershed-based conservation and recovery plans developed under ESA, salmon recovery plans developed under chapter 77.85 RCW, water resource plans developed under chapter 90.54 RCW, watershed plans developed under chapter 90.82 RCW, and a regional water supply plan or water resource management plan; c. The County’s Regional Wastewater Services Plan; and d. Other applicable provisions of countywide plans managed by King County, as specified in UTRC Guidance or checklists. | The UTRC did consider these issues and recommends approval of the Plan. |
| (42) | F-252: In reviewing proposals for modified and expanded service area boundaries for municipal water suppliers, the UTRC shall consider, in addition to Policy F-251: a. Compliance by the water system with its water system comprehensive plan, including water conservation elements; b. Whether it can meet its duty to provide service within its service area, as required under chapter 43.20 RCW; and c. Consistency with the service provisions of any applicable Coordinated Water System Plan, as adopted in King County Code Chapter 13.28. | The City is not planning to change its service area. |
| (43) | F-253: Consistent with Countywide Planning Policies, public drinking water system surface water reservoirs and their watersheds should be managed primarily for the protection of drinking water, but should allow for multiple uses, including recreation, when such uses do not jeopardize drinking water quality standards. Public watersheds must be managed to protect downstream fish and agriculture resources. | Not applicable. |
| (44) | F-254: Groundwater-based public water supplies should be protected by preventing land uses that may adversely affect groundwater quality or quantity to the extent that the supply might be jeopardized. The County shall protect the quality and quantity of groundwater used as water supplies through implementation of Policies E-493 through E-497 where applicable. | The County does and will continue to protect ground water by preventing land uses that may adversely affect groundwater quality or quantity. |