Breda Trolley Wire Upgrade

Business Case

Project Title: Breda Conversion project

Department/ Agency: Transportation/Transit

Project Number: A00480

Submittal Date: July 17, 2007

Business Need/ Problem Statement

Since 2000, Transit has been planning to replace the aging fleet of articulated electric trolleys by rebuilding dual powered buses (Bredas) that had been operating in electric trolley mode when traveling through the Downtown Seattle Transit Tunnel.  The trolley propulsion systems on these vehicles were determined to be sufficient to support normal street operation.  Rebuilding the vehicles was a cost effective way to update the age of the articulated trolley fleet and also provide an opportunity to expand the size of the fleet.  Cost for new vehicles was estimated to be more than $1-$1.2 million per vehicle, while the rebuild could be completed for $90,000.

Rebuild activities began in 2005 when the Downtown Seattle Transit Tunnel was closed and the Breda coaches were taken out of service.  As rebuilt vehicles were put into service, an issue developed with the amount of power being drawn by the vehicles and the effect that would have on the operation of the system.  While a number of steps were taken to reduce the power being drawn by the coaches, a number of simulations indicated that power issues would remain on the northern end of the trolley line unless additional power could be delivered to the system.

Background/ Overview

The Transit Division’s Capital Improvement Program (CIP) includes a project to convert up to 60 of the retired Bredas to operate solely in electric trolley mode.

The articulated electric trolleys are used on Routes 43, 44, 7 and 49 operating from Ballard through the University District and Capitol Hill to Downtown Seattle and south through the Rainier Valley.

This project was first included in the CIP in 2003 as a cost effective opportunity to replace Metro’s aging, high maintenance articulated trolley coaches.  A key consideration at the time was that the estimated cost for new articulated trolley buses was approximately $1-$1.2 million per vehicle.  Metro Transit staff had just successfully completed a remanufacturing process for the standard trolley coaches that resulted in substantial cost savings compared to the cost of purchasing new vehicles.

The first step in the process, completed in 2003, was to determine the feasibility of converting the Bredas to electric-only mode.  Metro Transit’s Vehicle Maintenance group completed an engineering assessment and developed a prototype vehicle.  Even though many of the diesel drive train components were worn out, the electric drives were still in good operating condition.  Initial testing of the prototype showed that the conversion would work.  Additional appropriation authority was obtained in 2004 and 2005 to convert the vehicles at an average cost of approximately $90,000 per vehicle.  This effort would also enable Metro Transit to slightly expand the size of the articulated trolley fleet to accommodate service growth.

Following the testing of the prototype vehicle, electrical tests were undertaken to evaluate the impact that this change in fleet would have on the trolley overhead power system.

Converted Bredas were tested to identify their electrical power requirements.  The prototype Breda bus has different electrical power and performance characteristics than the 20-year old articulated electric trolleys that were in operation.  As part of the conversion process, the diesel engine and fuel tanks were removed and changes were made to the brakes and heaters to reduce power consumption.  Despite these changes, testing showed that the electric power consumption was still higher than the existing coaches when pulling away from bus stops, particularly on hills.

To determine the effect that increased power consumption would have on the trolley overhead system, the Transit Division worked with electric systems consultant LTK Engineering to develop a model of the trolley power network.  The model network included details of the fleet’s power demands, updated route information, bus zone locations, street grades and frequencies of the trolley service.  The model testing demonstrated that the likelihood of service disruptions would increase in areas of the University District, Montlake, and along NE 45th Street to Ballard under certain conditions.  The testing also concluded that when all substations were on-line, no service disruptions should be experienced.  Six of the system’s thirty-three substations are located in the corridor of concern.  Similarly, testing demonstrated that service disruptions were not likely to occur at night and on the weekends when fewer coaches are in service.

Having one or more substations off-line is a relatively common condition for the trolley system.  Maintenance activities result in each substation on the line being down for four to five days once a year.  Unplanned substation shutdowns due to events like power disruptions or traffic accidents currently average three to four per month for the entire system.  Given current power consumption, the trolley system is usually able to operate during these events, although unplanned shutdowns can result in service disruptions.  With the increased power consumption of the reconditioned Breda coaches, the model testing determined that up to thirty eight coaches per month could experience service delays due to voltage drops unless changes were made to lower the power demand or increase the supply.

In response to questions raised by councilmembers and staff, Transit undertook additional testing of the system to validate the assumptions generated by the simulations.  To refine the study, actual substation outage data replaced the assumptions used in the simulation.  In addition, to verify how the reconditioned Bredas operate during substation outages, the coaches were field tested using various outage conditions.

The use of actual data demonstrates that substations do fail unpredictably for a number of reasons beyond Metro Transit’s control and the reconditioned coaches cannot operate under these low-voltage conditions.  The randomness and duration of outages highlight the fact that the situation is beyond Transit’s ability to respond with replacement buses or expediently restore service after a low-voltage incident.  The low voltage situations were most likely to occur during the peak period when the most passengers would be impacted.  Exhibit A shows the results of the tests.

The reconditioned coaches were field tested in November of 2006 to log their electric characteristics after the conversion and to monitor the effect of low voltage/substation outage conditions.  The test replicated peak hour conditions over 6 miles of trolley route. The results are presented below.   A summary of the test is included as Exhibit B.

The test ran four reconditioned Bredas over outage areas to represent the typical headways used on route 43, 44, and 49.  The instrumentation and observations results closely matched the simulation predictions and support the following conclusions.

- All substations operational in the north end:  Bredas operate normally.

- Planned substation outage (maintenance):  In general, Bredas will operate if headways are maintained; if bunched, especially on hills, it will cause them to lurch or to stop in place if the batteries don’t recharge.  If drivers are made aware of the situation, they should be able to maintain service through the outage condition.  However during the outage, the stress caused by areas of oscillating low voltage will shorten the life of the drive train.

- Unplanned substation outage:  Voltage “holes” will develop and cause sporadic trolley service disruptions or stoppages until Power & Faculties responds to jump the feeders.  Bredas will stop due to steep inclines, bunching, or because the batteries failed to recharge.  In areas of marginal voltage, the trolleys will begin to lurch and may or may not be able to continue service.  For example during the test, all Bredas stopped eastbound on N 46th Street and eastbound on NE Pacific Street equating to a full halt in trolley service.

Description and Causes of System Outages:

The possible causes of substation outages can be attributed to a variety of circumstances.  The most common occurrences are trolley poles coming loose, cross-connecting the overhead trolley wires, and causing a short.  A falling tree branch or other objects that contact the overhead wires can also cause a short.  These shorts are transient conditions that clear themselves but still require a service call to reset the substation.  A traffic accident, construction activity or a break in the wire can also cause the wire to fall to the ground.  The substation will then shut down the electrified wire for safety reasons.  The electrical supply side, Seattle City Light, can cause a substation shutdown when there is a power surge or a planned or unplanned loss in their power.  In some substations, the age of the equipment extends beyond 20 years and can fail without warning.  Equipment failures are rare but can produce the biggest impact because of the extended time required to find and install replacement breakers, switches, rectifiers, or transformers.

The most significant outage event during the observation period was the failure of a transformer in the Ballard area on May 26, 2005.  The substation was off line twice for 3 continuous days as repairs were made.  The trolley system did however operate normally during the transformer replacement, but if the Bredas were in service, this would not have been possible.  With the planned surplus of articulated MAN coaches, Metro Transit does not have a sufficient number of spare trolleys or diesel coaches to substitute for Bredas.  Service would be curtailed/reduced for the life of the outage.  In this recent case, that would mean 6 days of limited service around Seattle as buses are shuffled between routes.  Metro Transit would have limited success with substituting diesel for trolley buses, using 40-foot buses for articulated buses, increasing overtime, and decreasing route frequencies around the county to free up buses to use in the heavy ridership areas served by the trolleys.

Today, and in the future, following completion of the project, the trolley system will continue to be susceptible to wires breaking, trolley poles coming off the wire and other daily occurrences that disrupt trolley service.

Operational Response to System Outages:

King County Metro Transit has limited ability to rapidly respond to stranded trolley buses and customers, especially during peak-hours.  The type of response would vary based on the severity of the outage.  Options for response are discussed below:

Replacement Vehicles:  During peak service hours there are few, if any, diesel vehicles available to dispatch to the scene of a delay.  An additional constraint to using replacement vehicles is the ability to get the vehicle to the stranded coach with the traffic congestion that could result from a trolley being stopped in the street.  The use of diesel buses to replace trolleys would be an option to consider for outages that are of longer duration or are planned.

Manual intervention on street:  There are currently 3 service supervisors covering the entire north end during peak service hours.  If there was an outage of the trolley system, these supervisors would need to be moved from locations throughout the county to Downtown Seattle.  This could result in service disruptions in other areas of the system, in the event of accidents.  Depending on the location and availability of the service supervisors it could take 30 minutes or more for multiple staff to arrive on the scene.  With typical disruptions lasting a few minutes, the response would be to push the stranded trolley or trolleys clear of traffic until power could be resolved.

Manual intervention from communication center:  Currently, the trolley system operators communicate with the Communication Center using one of the 4 radio channels.  As a result, there is frequently a queue of operators waiting to talk to the Communication Center.  Operators talk to the Communications Center for a number of reasons including accidents, passenger incidents, and service disruptions.

Project Objectives and Outcomes, Benefits

Based on the confirmation obtained from field tests on the trolley system, this project would provide funding to accommodate changes in the electric trolley overhead power system to maintain schedule reliability of the trolley system.  This project will upgrade the conductors and overhead wire system along a 6-mile stretch of the existing trolley system.  Despite this increase, the total conversion cost of $12 million is significantly lower than the $60-$70 million cost that would have been required to purchase up to 60 new articulated trolley buses.

Constraints, Criteria, Dependencies

A key performance measure for the Transit system is on-time performance.  This is a measure of system reliability.  Transit’s 2007 target for on-time performance is 80%.  Through the first quarter of 2007, on-time performance was 75%.  Transit has been focusing efforts on improving this important measure.  Based on evidence from the testing and simulations, on-time performance of the articulated trolley fleet would be adversely impacted if this project were not undertaken, as trolley service would be disrupted.

Average weekday boardings on the articulated trolley fleet were 28,900 for the Spring 2007 service change based on data from the automated passenger counters.  This number excludes rides taken in the ride free area of Downtown Seattle, as well as customers on standard size trolleys that would be impacted by a service disruption.  These passengers rely on the bus system to predictably get them to their destinations based on published schedules.  Transit does not believe that it is acceptable to knowingly subject these passengers to service disruptions.

Maintaining or improving schedule reliability is a cornerstone of the transit program.  Over the years Transit has made a number of capital investments that were designed to improve schedule reliability.  These improvements include the ongoing maintenance of the system infrastructure to minimize the risk of system failures, replacing aging fleets and speed and reliability investments designed to improve travel times.

There are no impacts to other county agencies from this request, although reduced schedule reliability could generate more customer complaints to councilmembers and the Executive.

Risks

The electric trolley coaches operate on overhead wire that is strung along the trolley routes.  In the event that sufficient power is not available to a trolley anywhere along its route, the coach stops and cannot be moved unless power is restored, or the vehicle is physically pushed to a different location.  The electric trolley routes are some of the busiest in the transit system and they operate in highly congested areas of Seattle.  The disruption to passengers and vehicles in the vicinity of a coach that has lost power is significant to the individuals involved.  Passengers must wait until either power can be restored or a diesel bus can be dispatched.  Under these circumstances, riders are delayed and connections are missed.  Other traffic must maneuver around the stalled coach, if possible.  Similarly, any trolley coaches operating in either direction along the same stretch of the system would also stop, congesting traffic in both directions.

The lurching caused by a sudden loss of power to the reconditioned Breda’s could cause additional problems to drivers, passengers and equipment.  Drivers could become distracted and passengers jostled by the unexpected changes in bus speed.  The voltage/ acceleration fluctuations will damage the bus drive trains.

A schedule risk also exists since, optimally, the wire upgrade project needs to be completed in conjunction with coaches being rebuilt and available for service.  If the wire upgrade project cannot be completed coincident with rebuilt coaches going into operation, there could be problems.

Work Plan

The schedule for the project is dependent upon two elements:  timely acquisition of poles and permits from the City of Seattle.  Actual construction should be completed within 6-8 months following contract award.

Approach

The project will be managed internally, with consultant support for design and construction.  Permits are required from the City of Seattle for the work.

Cost

The cost of the project is estimated at $6.5 million.

Cost details, in thousands of dollars, are listed below:

Internal Staff Labor, Design and Construction                         $  550

Internal Staff Labor, Power and Facilities                                    471

Consultant (LTK) 						      220

Permit and City inspection during construction                             39

Steel Poles 							      320

Construction, includes 15% contingency *                   	   3,700

Contingency*							   1,200

*This is a relatively high contingency amount, supported by the Office of Management and Budget, to reflect the uncertainty about whether some of the overhead wires will need to be placed underground.  A significant effort will be undertaken to expend less than the budgeted $6.5 million.

Alternatives

Transit staff and the consultant (LTK) evaluated alternatives to mitigate the impact of the increased power requirements on system reliability.  These alternatives and the results of the evaluation included:

- Modifying the power consumption of the vehicles (heaters, lighting, etc.).  Changes were incorporated in the conversion process, but the changes were not sufficient to fully mitigate the problem.

- Installing additional power substations in affected neighborhoods.  Additional substations can be difficult to site and expensive to purchase and install, as a result, this alternative was deemed unfeasible and more costly and was not pursued further.

- Upgrading the conductors and overhead wire to improve the voltage that could be carried on the line.  Through the consultants work, this was determined to be the most feasible and lowest cost alternative to maintain system reliability.

Policy Links

This project supports the ongoing operation of the electric trolley system in Downtown Seattle.  Maintaining system reliability supports increased system ridership.

EXHIBIT A

Results of Substation Outage Testing

The table represents the impact to passengers if Bredas were in service during an outage and the effect the wire upgrade would have on service reliability.  The historical substation outage data was collected between May 2005 and February 2006.  Without the wire upgrade, the outage results demonstrate that trolley service would be impacted if the full complement of 59 Bredas were in service.  With the wire upgrade, the study confirms substation disruptions would not affect the operation of the trolley fleet and passengers during these same occurrences, as it is today.

| Actual Substation Outage Data Applied Against Planned Breda Trolley Service May 2005 through February 2006 (Peak-Times Only and does not include maintenance outages) |
| --- |
| Event (Substation Outage Time) | Location (Substation Name) (Impacted Routes) | Outage Duration | Cause | Number of Trolleys that would STOP mid-service | Number of Trolleys that STOP mid-service if the Wire Upgrades were Installed |
| 5/7/05 7:50am to 8:56am | U-District (Bob Sharp Sub) (70, 49, 44, 43) | 66 min | Unknown (Electrical short cleared when breaker reset) | 45 Trolleys | 0 Trolleys |
| 5/26/05 Outages over 12 peak periods | Ballard (W. Woodland Sub) (44/43) | 2 - 3 day peak-hour outages | Transformer failure (Down time for replacement work) | 432 Trolleys | 0 Trolleys |
| 6/10/05 5:45pm to 7:40pm | Ballard (W. Woodland Sub) (44/43) | 115 min | Unknown (Electrical short cleared when breaker reset) | 18 Trolleys | 0 Trolleys |
| 11/24/05 7:36am to 8:41am | U-District (Sharp/Jones Sub) (70, 49, 44, 43) | 65 min | Downed Guy wire | 7 Trolleys | 0 Trolleys |
| 12/13/05 8:30am to 9:01am | Capital Hill (Capital Sub) (43, 44) | 31 min | Unknown (Electrical short cleared when breaker reset) | 12 Trolleys | 0 Trolleys |
| Rider Impact only during Peak Hours |
| 51 Trolleys would Stop/Month (Under full service conditions) (Original Prediction - 38 Trolleys) | -0- Trolleys would Stop/Month (if the Trolley Wire Upgrade Work were Completed) |

EXHIBIT B

Breda Low Voltage Field Testing Results

(Substation Outage Impact on Northern Trolley Routes)

Summary:

The project team performed a field test to substantiate the analytical concerns over the traction power grid supporting Breda traffic.  The field test on November 19th mirrored peak hour conditions over 6 miles of trolley route during planned and unplanned substation outages.  The Breda’s performance was confirmed as unacceptable for passenger service during these outage conditions.  The team observed at least one and sometimes all four test Bredas stopping dead in the street, or within the marginal voltage areas the Bredas began to lurch.

Aside from verifying the analytical predictions, the “run to failure test” identified the effects to passengers, equipment, and service.  The Breda’s sudden loss of power or the lurching cause by too little power leads to:

- Drivers becoming distracted.

- Passengers jostled by the fluctuating changes in acceleration.

- The voltage/acceleration fluctuations damaging the drive trains.

- Breda batteries not charging at low voltages causing the trolley to stop in place.

- Not being able to maintain headway or worse case, leaving trolleys stopped in the street.

Operating Conditions:

The test ran four Bredas over outage areas to represent the typical headways used on route 43, 44, and 49.  The instrumentation and observations results closely matched the simulation predictions and support the following conclusions.

- All substations operational in the north end:  Bredas operate normally.

- Planned substation outage (maintenance):  In general, Bredas will operate if headways are maintained; if bunched, especially on hills, it will cause them to lurch or to stop in place if the batteries don’t recharge.  If drivers are made aware of the situation, they should be able to maintain service through the outage condition.  However during the outage, the stress caused by areas of oscillating low voltage will shorten the life of the drive train, which is already a problem due to a limited supply of spare parts.

- Unplanned substation outage:  Voltage “holes” will develop and cause sporadic trolley service disruptions or stoppages until Power & Faculties responds to jump the feeders.  Bredas will stop due to steep inclines, bunching, or because the batteries failed to recharge.  In areas of marginal voltage, the trolleys will begin to lurch and may or may not be able to continue service.  For example, during the test all Bredas stopped eastbound on N 46th Street and eastbound on NE Pacific Street equating to a full halt in trolley service.

Recommendation:

The team recommends the Wire Upgrade Project in the north end be approved.  The analytical study and field-testing confirm the weakness in the existing system and the risk to Metro Transit’s performance, equipment, and public perception.  The appropriation is in place to fund the project and the work could be done in phases to help mitigate the problem over the next year, 2007.