| # | Room | Location | Description |  |
| --- | --- | --- | --- | --- |
| 1 | 119 | Corridor, west of Kitchen | Wall bumper needed to protect wall from Kitchen door hitting it Agreed door stop/bumper should be added |  |
| 2 | 122/123/124 | Training Room/Kitchen/Break Room | Chair rails and corner protectors needed in and outside of these rooms Talking about covering lower part of wall with laminate (either same color as kitchen cabinet facing or lighter color used on window sills, or Acrovyn like existing corner protectors) rather than just chair rails and corner protectors. (Prefer lighter color: Pionite AT231 Suede, Manila Linen) |  |
| 3 | 126 | Corridor, east of Kitchen | Wall bumper needed to protect wall from Kitchen door hitting it Agreed door stop/bumper should be added |  |
| 4 | 137, 165 | Exercise Room Training Work Room | TV monitor wall mounts look like they may be pulling out of wall (or may have been that way all along due to tightening of mounting bolts/lag screws) Will check with WGClark about how they’re attached, but think it looks structurally sound. |  |
| 5 | 138, 142, 150 | Storage Room Server Room Radio Equip. Room | Humidifiers have had problems AND entire design has had problems resulting in water dripping onto computer equipment in Server Room. We have had some minor static problems recently in the Server Room. Acknowledged (and wasn’t aware that these were still a problem). No specific comments re: plan of action. Humidifiers remain shut down. |  |
| 6 | 142, 145, 146 | Server Room Dispatch Operations Secondary Operations | Floor drains under raised floor areas remain prone to sewage back-ups. (What happened to talk of installing removable plugs?) No plans to add these unless we have new problems. Have also had problems with occasional sewage odor backing up through drains. |  |
| 7 | 143 | Corridor, south wall | Wear/wall damage likely from powered wheelchair/cart (chair rails?) May repaint. |  |
| 8 | 143 | Corridor, north wall | Wear/wall damage likely from powered wheelchair/cart (chair rails?) Will check into having wall repaired and repainted. |  |
| 9 | 143 | Corridor by Restrooms | Two water fountains’ bottom plates never materialized. (FMD?) Will check to see if replacements can be found & installed. |  |
| 10 | 146 | Secondary Operations, west wall | Symon reader board’s left mounting screws don’t attach to anything solid; fear it could come down during even a minor earthquake (or, eventually, all by itself). At first unsure whether this was WGClark/Symon/KCSO issue. Ken explained that screws obviously didn’t attach to anything solid when we first removed the board for upgrade, so it was a problem from the beginning rather than one we created. Will talk to WGClark. |  |
| 11 | 152/153 | Restrooms | Series of sewer clogs/backups and recurrent “brown water” in toilets (and accompanying sewage odor in corridors) has affected all restrooms, though not all at the same time No specific plan of action but asked that we keep a log of problems. |  |
| 12 | 152/153 | Restrooms | Was tile grout (on walls and floors) ever sealed? Seems to absorb and hold water and cleaning liquids, and discolor unevenly. Not sure about sealing, but both think the discolorations are mildew and a maintenance issue. |  |
| 13 | 154 | Locker Room, north door | Wear likely from powered wheelchair/cart Noted. May repaint the door. |  |
| 14 | 158 | Double door to South Mechanical Yard from Electrical Room | Weather seal isn’t sufficient – can see daylight thru it and, during any significant rain, water enters the room and puddles on the floor. Will talk to WGClark about a fix. |  |
| 15 |  | Outside/landscaping | Some sprinkler heads installed too high making them prone to damage by lawn mowers, etc. (Several replaced by FMD.) Acknowledged. |  |
| 16 |  | Building exterior – north | Window trim above Comm Center office door appears loose Will talk to WGClark. |  |
| 17 |  | Building exterior – south | Some window trim & rubber strips on ballistic glazing (south wall of Room 146) have been loosening up and falling off. (Some fixed by RCECC staff & WG Clark) Will talk to WGClark. |  |
| 18 |  | South Mechanical Yard | Modifications that added cane rod assemblies were primed but not painted; hinges were also primed but not painted and are rusting. Talking about repainting primed areas. |  |
| 19 |  | East Parking Lot Gate | Parking gate card reader was replaced once and has been intermittently acting up again. Currently using temp replacement, which is also showing problems so FMD Security thinks there’s a wiring problem. Gate also goes through “phases” when it will almost close, then reverse (open), then almost close again. Sometimes it ultimately does close; other times it stops in the fully open position until someone uses manual controls to close it. Now it’s making loud screeching noises. (FMD’s looking into it.) Acknowledged; agreed that this sort of gate is inherently trouble-prone. |  |
| 20 |  | South Patio | Water “feature” pump has had a series of problems (has been out of service for 2+ months this time). FMD is in touch with KC Arts folks about it. Acknowledged. Has been in touch with Kirk (plumber) who’s working on it. UPDATE: Pump and plumbing has been reengineered and appears to be working properly. |  |
| 21 |  | Covered Walkway to East Parking Lot | Water leaks and runs down concrete wall in vicinity of card reader and disabled door opener box. It appears anytime there’s any significant rain. Appears to be problem with flashing above. Will talk to WGClark. |  |
| 22 |  | North wall of North Mechanical Yard | Sign fell off wall. (Combustible liquids warning) Treat as maintenance issue. |  |
| 23 |  | Tower | Brent Beden was trying to find tower info (specifically information on its lighting system) in the O&M documentation set and couldn’t find any. Was the tower handled separately or through W.G. Clark? Where would we find documentation? (Or was documentation even provided?) Looked through O&M manuals; agreed there probably should be something. Found sub-contractor (Strata) contact info and asked that we contact them directly for some documentation. |  |