Review of the City of Issaquah 2018 Water System Plan Update

Service Area The City of Issaquah (the City) owns and operates a municipal water system that primarily serves the City as well as unincorporated lands in King County contiguous with the City. Its water system provides service to an area that is largely coincident with the city limits (10.85 square miles) and potential annexation areas. The water distribution system serves the valley floors and parts of the surrounding hills. The City is surrounded by adjacent water utilities including City of Bellevue, Edgehill Water Association, King County Water District 90, and Sammamish Plateau Water & Sewer District (SPWSD), and it is unlikely the retail water service area will change in the future. The City's franchise number 8101 expired in 2010, and the city has initiated the renewal process. Water Use Efficiency In 2017, the City's water system provided service to a population of approximately 37,000. The population is projected to grow to 50,000 by 2027. On average from 2014 through 2016, single-family residence customers comprised 35 percent of total system water production, while multi-family residence and commercial customers have represented 19 and 21 percent, respectively. Approximately 15 percent of production is comprised of irrigation and public account usage. The remaining 10 percent of total water production is comprised of non-revenue water, with distribution system leakage accounting for 6.4 percent, less than the 10 percent state standard. The system wide average daily demand (ADD) was 2.61 mgd in 2017. By 2037, ADD is estimated to be 4.50 mgd. The water use efficiency goal for the City is to reduce the gallons per day for each equivalent residential unit (ERU) by five percent by the year 2026. The number of ERUs in 2010 was 17,395. The City has an average ERU use of 145 gallons per day (2016). The City's peaking factor is 1.94. The recent annual average distribution system loss is approximately five percent with a three-year average of 6.4 percent well within the ten percent goal from statute. The City's proprietary water system includes 13 reservoirs, 30 pressure reducing stations, 14 booster pump stations, six wells (two of which are not being used) and 135 miles of pipeline ranging in size from 4 to 16 inches in diameter. The City water system has four interties with the City of Bellevue, an emergency intertie with SPWSD, and two interties with Cascade Water Alliance's regional transmission main. The Plan contains a capital improvement plan with an estimated cost of approximately $53 million of investments through 2027, with an additional $8.3 million in the following ten-year period. The City identified funding sources for the proposed improvement projects which include rates, general facilities charges and bond proceeds. Reclaimed Water The City completed King County's Reclaimed Water Checklist and while recognizing the value of reclaimed water, does not currently use any reclaimed water. SEPA The City completed a State Environmental Policy Act (SEPA) checklist for the Plan and, as lead agency, issued a determination of nonsignificance for the issuance of the Plan on January 11, 2019. There were no appeals.

| A review of the specific statutes, rules, codes, and policies to the water system plan is as follows: |
| --- |
|  | A. General water plan, King County Code (KCC) 13.24.010 | Comments/findings |
| (1) | Review is applicable to utilities that obtain or distribute water in unincorporated King County under K.C.C. 13.24. Is there a need to meet the consistency requirements of RCW 43.20.260? | Yes, the City distributes water in unincorporated King County. The Plan is subject to King County Council approval. The Washington State Department of Health (DOH) needs to determine consistency of the Plan under RCW 43.20.260. |
| (2) | Consistency with King County Comprehensive Plan (KCCP) and development regulations, and policies including K.C.C. 21A.28.040 development standards, provision of adequate supplies for anticipated growth and development. | Yes, the Plan is consistent. |
| (3) | Infrastructure for existing and future service areas based on adopted land use map. | Yes. The City used adopted land use maps for that portion of the service area within unincorporated King County. |
| (4) | Review proposals for modified or expanded service areas based on compliance with utility's approved plan, and ability to meet duty to serve requirement. | The City's retail water service area was originally specified in the East King County Coordinated Water System Plan. Updates to that plan and subsequent agreements with adjacent purveyors have resulted in the current service area. The retail service area is not expected to change in the future due to the geography of the surrounding areas and because all of the surrounding areas are currently served by other water purveyors. |
| (5) | Sufficient information to demonstrate the ability to provide service consistent with the requirements of all applicable statutes, codes, rules, and regulations. | Yes, the Plan demonstrates an ability to provide service consistent with applicable statutes, codes, and regulations. The City obtains its water primarily from ground water and interties with the Cascade Water Alliance. The City's water supplies are sufficient to meet projected peak day demand in 2020. |
| (6) | Monitor and review effectiveness of purveyor conservation plans if within area covered by an approved coordinated water system plan (CWSP). | The City's conservation program meets minimum state requirements. |
|  | B. Consistency requirements: 13.24.060 |
| (7) | State and local health requirements. | Yes. |
| (8) | Creation and maintenance of logical service areas. | Yes, the service area is logical. |
| (9) | Elimination or prevention of duplicate facilities. | Yes. |
| (10) | Promotion of most healthful and reliable services to the public. | Yes. Water purveyed by the City complies with public health standards. The well water is chlorinated but not fluoridated. Water obtained from the Cascade Water Alliance is chlorinated and fluoridated. |
| (11) | Provision of service at a reasonable cost and maximization of use of public facilities. | Yes, the City's rates for water service are comparable to the rates charged by similar utilities. |
| (12) | KCCP and other pertinent county adopted plans and policies. | Yes, there is consistency between the City's plan and the KCCP. |
| (13) | Basin-wide or multi-basin water plans, sewerage plans, or both when approved by the Washington State Department of Ecology (Ecology) or DOH. | No multi-basin water plans are applicable. |
| (14) | Applicable state water quality, water conservation, and waste management standards. | Yes, applicable water quality standards are met. The three-year rolling average distribution system leakage (DSL) is estimated at 6.4 percent, which is less than the ten percent requirement established under the Municipal Water Law. |
| (15) | Water Resources Act (RCW 90.54). | The Plan makes no connection with the requirements of RCW 90.54.180 or RCW 90.03.386. The City will maintain its existing conservation (efficiency) program to comply with DOH’s Water Use Efficiency Rule. |
| (16) | Growth Management Act (GMA) (RCW 36.70A). | The City's water service area includes unincorporated urban areas. The City appropriately used King County land use zoning for these areas. |
| (17) | Groundwater management plans. | The City has a Wellhead Protection Program. |
| (18) | Federally approved habitat conservation plans and recovery plans under the Endangered Species Act (ESA). | Not applicable. |
| (19) | Requirements for salmon recovery under Ch. 77.85 RCW, and other plans, including regional water supply or water resource management plans. | The City participates in salmon recovery processes in King County under the framework of chapter 77.85 RCW. |
| (20) | Applicable requirements to evaluate opportunities for the use of reclaimed water under chapter 90.46 RCW and CO-7. | The City has evaluated reclaimed water use but does not use reclaim water. |
|  | C: King County Comprehensive Plan—consistency with provisions and specific policies. |
|  | COUNTYWIDE PLANNING POLICIES |
| (21) | FW-5: management of resources for multiple beneficial uses, including flood and erosion hazard reduction. | Not applicable. |
| (22) | FW-12(c): ensure sufficient water supply for growth and fish habitat needs through long-term planning. | Sufficient water supply for projected growth is available. |
| (23) | CA-5, CA-6, and E-434 and policies to protect quantity and quality of groundwater. | Yes, the City has policies in place to protect groundwater sources. |
| (24) | CO-5: water supply shall be regionally coordinated. | Yes, the City's water supply is regionally coordinated. |
| (25) | CO-6: aggressive conservation efforts shall be implemented. | The City's conservation program meets minimum state requirements. |
|  | KING COUNTY COMPREHENSIVE PLAN POLICIES |
| (26) | F-107: Plan for provision of services to rural areas. | The City does not provide water to the rural area. |
| (27) | F-108: King County to work with cities and service providers to establish priority areas for public funding of capital facilities. | The capital improvement program (CIP) is adequate and appropriately focused with funding sources identified. |
| (28) | F-201: All facilities and services should be provided in compliance with provisions and requirements of the Endangered Species Act and the Clean Water Act. | The City has planning policies which develop, implement, monitor and adapt: programs, procedures and practices to improve and protect water quality, habitat, the aquifer and other environmental values in areas where the City must construct, operate, maintain, or replace water system infrastructure. (ICP Policy U-C11 Environmental Protection) |
| (29) | F-209: support rural levels of development and not facilitate urbanization. | The City is committed to serving the area consistent with land use. |
| (30) | F-210: capital facility plans and improvement programs for services to unincorporated King County are consistent with the KCCP. | Yes, the CIP is consistent with the KCCP. |
| (31) | F-211: King County helps coordinate development of utility facilities. | Yes, to the extent applicable, King County will do this. |
| (32) | F-221: King County shall initiate a sub-area planning process with any service provider that declares, in its capital facilities plan, an inability to meet service needs within service area. | Not applicable. The City did not identify any inability to meet service needs within its service area. |
| (33) | F-223: If a service deficiency is identified in a service provider's existing service area, King County and the applicable service provider shall remedy the deficiency through a joint planning process addressing capital improvement programs and long-term funding strategies reuse programs. | Not applicable. The City did not identify any inability to meet service needs within its service area. |
| (34) | F-231: King County supports coordination of regional water supply planning, sales of excess water supplies among municipalities in the region, water quality programs and water conservation, reuse and reclaimed water programs. | Yes, the City supports regional water supply coordination. |
| (35) | F-232: Water utilities that obtain water from, or distribute water in unincorporated King County, and water utilities formed as special purpose districts under Title 57 RCW are required to submit water system plans to the county for review and approval and shall describe in their plans how they intend to meet their duty to provide service within their retail service areas. | The City distributes water in unincorporated King County so the plan is subject to review and approval by the King County Council. The City is committed to meeting its duty to serve in its retail service area by direct service. |
| (36) | F-243: public drinking water system reservoirs and watersheds should be managed primarily to protect drinking water supplies, but allow multiple uses when not jeopardizing water quality; downstream uses including recreation, fish, and agricultural resources. | Not applicable. |
| (37) | F-244: groundwater supplies should be protected by preventing land uses that may adversely affect quantity or quality. | The City prepared and DOH approved a Wellhead Protection Program. The Wellhead Protection Program is documented with this Plan and will be incorporated in to the County's critical areas ordinance with the next update. |
| (38) | F-246: King County supports interties that allow the transfer of water resources among water utilities to meet the projected demands for growth where such interties meet the requirements of RCW 90.03.383 and are also consistent with any applicable locally adopted comprehensive plans, regional water supply plans, adopted groundwater management plans, watershed plans, approved Coordinated Water System Plans, Endangered Species Act response requirements and Clean Water Act requirements. | The City has several interties with utilities that are consistent with locally adopted comprehensive plans for the distribution of water to meet project growth demands. |
| (39) | F-249: Utilities with more than one thousand service connections required to submit water system plans for approval to King County shall include an evaluation of reclaimed water use opportunities by completing King County's Water Reclamation Evaluation. | The City has more than 1,000 service connections and completed King County's Water Reclamation Evaluation Checklist. |
| (40) | F-251: In its review of water system plans, the UTRC shall consider the criteria provided in KCC 13.24.010, 13.24.060, and 13.24.070, and determine the plan’s consistency with the following: a. Applicable provisions of the King County Comprehensive Plan, land use plans, and development regulations adopted under the Growth Management Act; b. Approved or adopted regional water resource plans, such as basin plans, groundwater plans, watershed-based conservation and recovery plans developed under ESA, salmon recovery plans developed under chapter 77.85 RCW, water resource plans developed under chapter 90.54 RCW, watershed plans developed under chapter 90.82 RCW, and a regional water supply plan or water resource management plan; c. The county's Regional Wastewater Services Plan; and d. Other applicable provisions of countywide plans managed by King County, as specified in UTRC Guidance or checklists. | The UTRC did consider these issues and recommends approval of the Plan. |
| (41) | F-252: In reviewing proposals for modified and expanded service area boundaries for municipal water suppliers, the UTRC shall consider, in addition to Policy F-251: a. Compliance by the water system with its water system comprehensive plan, including water conservation elements; b. Whether it can meet its duty to provide service within its service area, as required under chapter 43.20 RCW; and c. Consistency with the service provisions of any applicable Coordinated Water System Plan, as adopted in King County Code Chapter 13.28. | The City is not planning to change its service area. |
| (42) | F-253: Consistent with Countywide Planning Policies, public drinking water system surface water reservoirs and their watersheds should be managed primarily for the protection of drinking water, but should allow for multiple uses, including recreation, when such uses do not jeopardize drinking water quality standards. Public watersheds must be managed to protect downstream fish and agriculture resources. | Not applicable. |