| Review of Covington Water District 2007 Water System Plan Update |
| --- |
|  | A. General and water plan-specific: King County Code 13.24.010; 13.28 | Comments/findings |
| (1) | Applicable to special purpose districts (RCW Title 57) and water utilities distributing or obtaining water in unincorporated King County. | Covington Water District (CWD) both obtains and distributes water in unincorporated King County. |
| (2) | Consistency with King County Comprehensive Plan and Development regulations, and policies [including King County Code 21A.28.040 development standards, provision of adequate supplies for anticipated growth and development]. | Generally the water system plan (WSP) is consistent except as noted. |
| (3) | Infrastructure for existing and future service areas based on adopted land use map. | The WSP recognizes adopted land uses established by the Cities of Covington, Maple Valley, and Black Diamond and King County. Hydraulic modeling to assess the system under present demand and future anticipated demand to meet peak hour and fire flows was done. The model results indicated that both under current and future demand conditions there are isolated areas that do not meet minimum pressure requirements for both peak hour and fire flow. The capital facilities program focuses on new facilities for the identified deficiencies. The infrastructure is adequate for the service area with in existing city boundaries, and existing wholesale customers. The consistency checklists were completed by City of Covington and City of Maple Valley to affirm consistency between CWD proposed action and their development plans. The City of Black Diamond did not complete a consistency checklist. CWD was asked by Washington State Department of Health (DOH) to again seek a City of Black Diamond consistency statement. CWD states a commitment to ultimately provide service to all customers within the service area boundary in keeping with the adopted South King County Coordinated Water System Plan. The WSP did not identify a retail service area to provide assured supply within the service area overlaid by unincorporated King County. In response to Utilities Technical Review Committee (UTRC) comments the District defined its retail service area to be coincident with its corporate boundary. Reviewed by King County Department of Transportation. |
| (4) | Review proposals for modified or expanded service areas based on compliance with utility’s approved plan, and ability to meet duty to serve requirement. | No service area changes identified in WSP. Proposed modification or expansion of the system to address hydraulic deficiencies will assist the utility in meeting its duty to serve requirements. |
| (5) | Sufficient information to demonstrate the ability to provide service consistent with the requirements of all applicable statutes, codes, rules, and regulations. | In general, the Plan appears to meet this requirement; reviewed by Seattle King County Public Health (SKCPH). DOH comments on draft plan; no comments from the Washington State Department of Ecology (DOE). On the provision of “timely and reasonable” service within retail service area the plan is silent. CWD did provide supplemental information to King County during UTRC review. In general, the District understands “timely” to mean provision of service within 120 days after an agreement for service is reached. With regard to the “reasonable” element of the clause the District views this to mean service is reasonable if: a condition of service is consistency with local land use plans and development regulations; the conditions of service and associated costs are consistent with the conditions of service described in the Plan; and the conditions of service and associated costs are consistent with experiences of other applicants requesting similar service. The District does not intend to publish the above information in the water system plan. Therefore the proposed ordinance includes a finding that contains the supplemental information the District filed with the UTRC to ensure the public has access to the information. |
| (6) | Monitor and review effectiveness of purveyor conservation plans if within area covered by an approved Coordinated Water System Plan (CWSP). | Per capita consumption has been reduced over time and appears to be a reasonable number. Non-revenue water includes water used for non-billed purposes and water lost by leakage and for the time period 1999 – 2004 the average is 12 percent; no specific program is outlined to address as required under State law. In working with the UTRC the District committed to develop a program to address unaccounted for water during the next water system plan update. |
|  | B. Consistency requirements: 13.24.060 |  |
| (7) | State and local health requirements . | DOH commented on water system plan June 23, 2007. DOH staff indicated a willingness to approve the plan upon King County approval. |
| (8) | Creation and maintenance of logical service areas. | Generally yes. The 53 square mile service area does encircle numerous areas where the CWD does not supply water. There are 14 Class A public water systems two of which CWD provides satellite system management to some degree. There are 130 Group B public water systems in the service area. No change to the service area boundary is proposed. |
| (9) | Elimination or prevention of duplicate facilities. | Generally yes. Pursuant to state law, and King County Code approval of new Group B systems by Seattle King County Public Health (SKCPH) will be conditioned with the requirement to be satellite owned or managed. The plan and CWD Administrative Code are not clear on requiring satellite management for indirect service or service in the future when the infrastructure is further built out. |
| (10) | Promotion of most healthful and reliable services to the public. | Significant investments in water quality and treatment of some of CWD’s sources. |
| (11) | Provision of service at a reasonable cost, and maximization of use of public facilities. | The WSP is silent on the criteria CWD will use to determine their approach to delivering service in a “timely and reasonable” manner under RCW 43.20.260. See number five above. CWD has a rate structure to encourage efficiency of water use during the summer months. |
| (12) | King County Comprehensive Plan, and other pertinent county adopted plans and policies. | There is consistency between CWD’s WSP and the South King County Coordinated Water System Plan. |
| (13) | Basin wide or multibasin water plans, sewerage plans, or both when approved by DOE or DOH. | CWD has well head protection programs for their ground water sources and is consistent with the South King County Ground Water Management Plan. The WSP mentions salmon recovery and listed species but provides no information on how operations of the CWD will support salmon recovery. |
| (14) | Applicable state water quality, water conservation, and waste management standards. | Meets state water quality standards. CWD is a member of the Cascade Water Alliance and has developed a water conservation program in concert with its regional partners. The WSP does not propose a plan to address unaccounted for water that is about 12 percent (averaged over the past few years) percent of total water produced. In working with the UTRC the CWD has agreed to create and implement an appropriate unaccounted for water program. |
| (15) | Water Resources Act (RCW 90.54). | No comments yet from DOE. |
| (16) | Growth Management Act (GMA) (RCW 36.70A). | The WSP uses Puget Sound Regional Council population and employment growth forecasts appropriately. Not clear whether concurrency requirements will be met with in complete service area especially for fire flow in certain areas. |
| (17) | Groundwater Management Plans. | Groundwater management plan implementation in County is not active in South King County. |
| (18) | Federally-approved habitat conservation plans and recovery plans under the Endangered Species Act (ESA). | See #19. |
| (19) | Requirements for salmon recovery under RCW 77.85, and other plans, including regional water supply or water resource management plans | A salmon recovery plan under chapter 77.85 RCW was developed for the Green River basin. Numerous tributaries within the service area of CWD contribute flow to Soos Creek and the middle Green River. The WSP mentions salmon recovery and listed species but provides little on how operations of the CWD will support salmon recovery. |
| (20) | Applicable requirements to evaluate opportunities for the use of reclaimed water under chapter 90.46 RCW. | CWD did an investigation of reclaimed water opportunities and identified potential uses on golf courses and school grounds. CWD is actively pursuing opportunities with King County. |
|  | C. King County Comprehensive Plan—consistency with provisions and specific policies (Water System Plan) |  |
|  | COUNTYWIDE PLANNING POLICIES |  |
| (21) | FW-5: management of resources for multiple beneficial uses, including flood and erosion hazard reduction. | No apparent relevance. |
| (22) | FW-12: ensure sufficient water supply for growth and fish habitat needs through long-term planning. | Recognizes need to develop additional supplies for long-term growth, and is developing plan. No direct plans for protecting or restoring fish habitat or instream flows that may be impacted by Witte Road or 222nd well fields. |
| (23) | CA-5 and CA-6: Adopt policies to protect quantity and quality of ground water. | DOH appears to be satisfied with wellhead protection program under DOH regulations. |
| (24) | CO-5: water supply shall be regionally coordinated. | CWD is working with Tacoma Public Utilities and Cascade Water Alliance for long-term supply. |
| (25) | CO-6: aggressive conservation efforts shall be implemented. | The CWD conservation program has reduced per capita water consumption; no data to determine if the goal from the CWSP was met. CWD completed a conservation potential assessment in 2002 and plans further efforts. Not clear what the impact of DOH water use efficiency rule will be. There is no explicit goal in light of the water use efficiency rule and that goals must be set by the beginning of 2008. As a partner in the Second Supply Project with Tacoma (and others) the CWD agreed to promote increased water use efficiency, including achieving a cumulative aggregate (total retail and wholesale) reduction in water use by 10 percent over a ten year period beginning January 1, 2000. This requires a 10 percent reduction in projected levels of consumption by January 1, 2011 using the year 2000 consumption rates as a basis for projections. |
| (26) | CO-7: water reuse and reclamation shall be encouraged, especially for high water users. | See # 20 above. CWD is considering using reclaimed water and has inventoried the largest water users. CWD also tracks outside irrigation use and requires irrigation meters for outside use on all new development. Largest water users are schools (70 percent outdoor use) and one golf course. |
|  | KING COUNTY COMPREHENSIVE PLAN POLICIES |  |
| (28) | E-119: management and protection of water resources by King County through incentives, regulations and programs. | Generally yes. |
| (29) | E-123: protect and enhance surface waters, including Puget Sound. | New Puget Sound Strategy calls for increased use of reclaimed water in order to reduce discharges; there is no direct relationship to CWD as it does not manage wastewater. CWD is exploring with the County the use of a skimming plant and generation of reclaimed water in the district. |
| (30) | E-155: protect groundwater, and develop strategies to compensate or mitigate for losses. | CWD has a wellhead protection program focused on water quality. No strategy in place to compensate or mitigate if ground water quality problems arise. |
| (31) | E-204: protect critical habitat. | No apparent relevance. |
|  | F-102: King County will provide or manage countywide services, which include waste water, water resource management, surface water management, flood warning and floodplain management, protection and preservation of natural resource lands. | Cities within the service area of CWD participate in the surface water management program, and will participate in countywide flood control district. |
| (32) | F-104: plan for provision of services to rural areas. | See above in regards to CWD’s plans for service delivery in its retail and future service area. |
| (33) | F-105: King County work with cities and service providers to provide services. | King County is willing to work with CWD on updating South King CWSP in regards to greater assurance of service delivery in unincorporated King County. |
| (34) | F-201: all facilities and services should be provided in compliance with provisions and requirements of the ESA. | Not apparent whether CWD evaluated potential exposure under ESA for its activities. See # 20 above. |
| (35) | F-202: ensure adequate supply of public facilities to support communities. | Capital program to ensure adequate capacity in retail and wholesale areas (existing customers) especially for fire flow. |
| (36) | F-203: King County will work with cities, special purpose districts, and other service providers to define regional and local services and determine appropriate providers. | The CWD has a strategy for provision of satellite management in unincorporated areas, per Coordination Act, other state laws, and King County policies. |
| (37) | F-207: support rural levels of development and not facilitate urbanization. | Development in rural areas will be limited to individual supplies or very small systems and satellite management of small systems. CWD has policies in place to be the satellite manger in unincorporated areas, per Coordination Act, other state laws, and King County policies. |
| (38) | F-208: capital facility plans and improvement programs for services to unincorporated King County are consistent with King County Comp Plan. | The Plan has been supplemented to define a retail service area to be the external boundary of CWD in the South King County CWSP. DOH developing rules that may help define the duty to serve. |
| (39) | F-209: King County helps coordinate development of utility facilities. | King County is willing to work with CWD on this issue in rural areas. |
| (40) | F-211: King County capital improvement program shall show that projected need for services and facilities in Urban Growth Areas (UGAs) can be met in compliance w/concurrency requirements of GMA. | King County comp plan may need to note areas within unincorporated King County where designated water service providers will be unable to supply water. |
|  | F-212: water and sewer utilities providing service to unincorporated King County shall prepare capital facility plans consistent with requirements of GMA and the King County Comp Plan. | The capital facility plans appears consistent with requirements of GMA and the King County Comp Plan. |
| (41) | F-214: King County shall initiate a sub area planning process with any service provider that declares, in capital facilities plan, an inability to meet service needs w/in service area. | CWD is committed to providing service to those in its service area. |
| (42) | F-216: where an area wide sewer, water, or transportation deficiency is identified, King County and applicable service providers shall remedy the deficiency through a joint planning process. | No area wide sewer or water deficiency identified. |
| (43) | F-224: King County supports coordination of regional water supply planning, sales of excess water among municipalities, water quality programs, and water conservation and reuse programs. | See generally above for description of relevant provisions of CWD plan. CWD is supporting regional efforts with City of Tacoma and Cascade Water Alliance. |
| (44) | F-225: Group A water systems must meet duty to serve requirement w/in service area as defined under CWSP or by individual water system plans. | See discussion above re adequacy of proposed water service w/in CWD’s “future” service area; plan to address “retail” service area is deficient as retail service area is not defined. Plan amendment may be required, depending on outcome of DOH rulemaking on duty to serve. |
| (45) | F-226-230: Provides a hierarchy of water supply providers in unincorporated King County, depending on whether within UGA or rural areas, with preference for providing water from existing suppliers. | CWD’s plan is consistent with this hierarchy in regards to provision of service with in the UGA and South King CWSP. May need to develop a strategy for Group B systems within the service area. |
| (46) | F-231: Service from exempt wells limited to subdivisions with no more than six lots, and limited to one well unless an additional well is needed for flow requirements for the six lots; water from the exempt well is limited to no more than one-half acre irrigation. | Generally applicable to water service delivery by CWD. Given the number of Group A and Group B public water systems within the service area of CWD it is not apparent CWD is managing small systems within unincorporated King County and within its future service area. |
| (47) | F-233-235: develop regional water supply plan with a role for reclaimed water as a source of supply. | CWD is participating as a member of the Central Puget Sound Forum in regional water planning and participated on regional planning technical committees. |
| (48) | F-236: King County supports the use of interties consistent with planning, and implement approved ESA and CWA response requirements. | CWD pursued a long-term agreement with Tacoma as a partner for use of second supply project water delivered by intertie consistent with this policy. Tacoma water supplies fall within Tacoma’s HCP developed under the ESA, and withdraws are made from its surface water sources consistent with agreements with the Muckleshoot Indian Tribe. See above re ESA relevance. CWD also has interties with Cedar River Water & Sewer District as well as City of Auburn. |
| (49) | F-239: King County partner with utilities to encourage best management practices and conservation through such means as developing reclaimed water, aggressive water conservation and reuse measures; support planned land uses with reliable service at minimum cost; encourage reclaimed water use, focused on large water users such as golf courses and cemeteries. | King County is willing to work with CWD on these issues, particularly appropriate use of reclaimed water, and provision of water service in unincorporated areas at affordable price. |
| (50) | F-240: UTRC to consider (a) consistency with land use plans and development regulations; (b) approved or adopted plans for groundwater, ESA, salmon recovery, water resources, watershed planning, regional water supply plan; and (c) the Regional Wastewater Services Plan. | See above for UTRC comments. |
| (51) | F-241: In reviewing proposals for modified and expanded service area boundaries, UTRC must include an evaluation of the utility’s compliance with its comprehensive water system plan, including water conservation elements, and whether it can meet its duty to provide service; no approval of service area where unable to provide service for reasons in RCW 43.20.260. | CWD is not proposing to modify or expanded service area boundaries. King County has pointed out in its comments to CWD on the need for further clarification on definitions of “retail service area” and “duty to serve” requirements and has addressed this as conditions of the ordinance approving the Plan. |
| (52) | F-242: UTRC to develop a water accounting system, in conjunction with water utilities, to ensure the ability of utilities to issue certificates of availability. | Not yet developed although CWD does use water availability certificates. |
| (53) | F-243: public drinking water system reservoirs and watersheds should be managed primarily to protect drinking water supplies, but allow multiple uses when not jeopardizing water quality; downstream uses including recreation, fish, and agricultural resources. | No substantial relevance to CWD. |
| (54) | F-244: groundwater supplies should be protected by preventing land uses that may adversely affect quantity or quality. | Should be addressed in City of Covington, City of Maple Valley, and City of Black Diamond GMA comprehensive plan. CWD does have a wellhead protection program. |