| Review of City of Redmond General Sewer Plan, November 2009 |
| --- |
|  | A. General and sewer plan-specific: King County Code 13.24.010 | Comments/findings |
| (1) | Applicable to special purpose districts (Revised Code of Washington (RCW) Title 57) or sewer utilities that provide sewer collection or treatment in unincorporated areas of King County. | A portion of the City of Redmond’s (City) service area lies within unincorporated King County. |
| (2) | Submitted every six years or sooner if required by the Washington State Department of Health (DOH) or the Washington State Department of Ecology (DOE), or whenever sewer conditions have changed significantly within sewer service area. | The City’s last sewer plan (Plan) was approved by King County in 1997, Ordinance 12964. The City did amend the sewer plan in early 2009 and that amendment was approved by the King County Council by Ordinance 16578. |
| (3) | Meets criteria in RCW chapter 90.48 RCW as well as King County Code (KCC) as follows: (1) compliance with the development program outlined in the King County Comprehensive Plan; (2) compliance with the basin wide water and/or sewerage plan; and (3) compliance with policies in the King County Comprehensive Plan for water and/or sewage facilities. | Yes. See below for each of the criteria. |
| (4) | Consistency with King County Comprehensive Plan and development regulations, and policies. | Yes. See below for details. |
| (5) | Infrastructure for existing and future service areas based on adopted land use map. | Yes, for that portion of the service area in unincorporated King County. Land use for the County, and other local governments, is described. |
| (6) | Sufficient information to demonstrate the ability to provide service consistent with the requirements of all applicable statutes, codes, rules, and regulations. | Yes. See below for details as to existing facilities and plans for improvements. The City utilized a new system hydraulic model to evaluate its collection capacity, and concluded that there is adequate capacity to accommodate peak flows and anticipated growth to the year 2028. |
| (7) | Consistent with Washington Administrative Code (WAC) 173-240-050. | Yes. DOE has approved the November 2009 Plan as consistent with WAC 173-240 and RCW 90.48.110. |
| (8) | Discuss the following: Existing and planned flows average and peak. Existing and planned flows for any basin discharging into County system. Amounts of inflow and infiltration (I/I), in comparison with County standard of 1,100 gal/acre/day, and steps being taken to reduce. Areas of concern regarding corrosion and odor control, and steps being taken. Opportunities for reclaimed water. Additional information required by the Utilities Technical Review Committee (UTRC). | All are discussed in the Plan. The City worked with King County Wastewater Treatment Division (KCWTD) on the regional I/I control program. The City does have some sewer sub-basins with high I/I and has committed to continued to work with KCWTD as initial I/I control projects are implemented and monitored for effectiveness. There were no issues identified with either corrosion or odor control. There are opportunities for use of reclaimed water within and near the City. The City has worked cooperatively with the County to evaluate and implement, if feasible, reclaimed water projects. The City is a member of the Cascade Water Alliance (Cascade); Cascade conducted an assessment that shows a potential use of 2.77 million gallons of reclaimed water for Cascade’s service area. In its review of the Plan, the UTRC asked for additional information, which has been provided by the City either in the final Plan or in direct communication with the UTRC. |
|  | B. Public Sewer Service: 13.24.035 |  |
| (9) | All developments within Urban Growth Area (UGA) served by sewer unless on-site are allowed as temporary per KCC 13.24.136 and 13.08.070. | Yes. There are unserved areas within the City’s service area, and the City has a program to extend service to those areas. The City’s service area is largely already developed, with new development limited principally to mixed-use development and redevelopment construction. The City anticipates the residential population served to grow from 61,000 in 2008 to approximately 89,000 by 2028. |
| (10) | Public sewer provided in rural towns if approved by King County. | Not applicable. |
| (11) | No public sewer service outside UGA unless authorized under KCC 13.24.134. | All within the UGA except for service to the Wilder Elementary School as authorized by Ordinance 16578. |
| (12) | Sewer service extensions to be approved by King County Council, if consistent with KCC 13.24.035 and County polices and regulations, in the form of a sewer plan or amendment. | None planned. |
| (13) | Required elements of sewerage general plan, as called for in RCW 36.94.010(3), are included in King County Comprehensive Plan and Technical Appendix. | Yes. |

|  | C. Consistency requirements: 13.24.060 |  |
| --- | --- | --- |
| (14) | State and local health requirements. | The Plan has been reviewed and approved by DOE, with responses to DOE’s comments incorporated into the revised Plan. The UTRC review process included a representative of Public Health-Seattle and King County. |
| (15) | Elimination or prevention of duplicate facilities. | The City has written agreements with other sewer providers as to areas to be served in order to avoid overlapping jurisdiction. |
| (16) | Promotion of most healthful and reliable services to the public. | Yes. |
| (17) | Provision of service at a reasonable cost, and maximization of use of public facilities. | Sewer rates appear reasonable. |
| (18) | Reduction of number of entities providing sewer service in King County. | The City has other agreements with local general purpose governments and adjacent Woodinville Water District regarding sewer service, and anticipates that its entire service area will ultimately be served by sewers. No other entities provide sewer service within its service area. |
| (19) | King County Comprehensive Plan and other pertinent County adopted plans and policies. | Yes. See below. |
| (20) | Basin wide or multibasin water plans, sewerage plans, or both when approved by DOE or DOH. | The City is aware of, and supports, the planning done for the Cedar, Sammamish, and Lake Washington basin for salmon recovery purposes. The City is part of the regional wastewater system managed by King County. |
| (21) | Applicable state water quality, water conservation (e.g., RCW 90.48.495), and waste management standards. | Yes. The Plan has been approved by DOE. There is no indication in the Plan as to whether the City’s planned water conservation efforts would reduce flows into its sewerage system or have any impact on its conveyance capacity. |
| (22) | Growth Management Act (GMA) (RCW 36.70A). | Yes, the Plan is consistent with the King County Comprehensive Plan. |
| (23) | Groundwater Management Plans. | The City is actively implementing a neighborhood sewer replacement program to connect areas served by on-site septic systems to the regional sewer system. Those actions should reduce public health risk from failing septic systems to underlying aquifers. |

| (24) | Federally-approved habitat conservation plans and recovery plans under Endangered Species Act (ESA). | The Plan makes no reference to the salmon recovery efforts within the watershed. However, the City has participated in the salmon recovery effort for Water Resource Inventory Area 8. |
| --- | --- | --- |
| (25) | Requirements for salmon recovery under RCW 77.85, and other plans, including regional water supply or water resource management plans. | See number 24. |
| (26) | Applicable requirements to evaluate opportunities for the use of reclaimed water under chapter 90.46 RCW. | Yes. See above. The Plan explicitly states the City’s support for regional efforts to address the feasibility of reclaimed water for nonpotable purposes, and for King County’s role as a wholesale supplier of reclaimed water. |
|  | D. Facilities crossing rural areas: KCC 13.24.132: Sewer facilities allowed crossing rural areas only under certain conditions. | Complies with the KCC. No rural areas within the City. The City’s service line from Novelty Hill does traverse the rural area consistent with the KCC. |
|  | E. Facilities in rural and natural resource areas, KCC 13.24.134: Only for schools or public health emergencies, under certain conditions. | Complies with the KCC. No rural areas within the City. The City does provide sewer service to the Wilder Elementary School which is located in the rural area. The King County Council approved the connection by ordinance 16578. |
|  | F. State Environmental Policy Act documentation. | Determination of Nonsignificance issued by the City on July 31, 2009 with no appeals. |
|  | G. King County Comprehensive Plan—consistency with provisions and specific policies (Sewer System Plan). | See below. |
|  | COUNTYWIDE PLANNING POLICIES |  |
| (27) | CA-5 and CA-6: adopt policies to protect quantity and quality of groundwater. | I/I program to be enhanced, as described above. Connection of houses and businesses with on-site septic to the City’s sewer system should reduce health risks from any failing septic systems. |
| (28) | CO-7: water reuse and reclamation shall be encouraged, especially for high water users | See above. |
|  | KING COUNTY COMPREHENSIVE PLAN POLICIES |  |
| (29) | F-104: plan for provision of services to rural areas. | No rural areas within the City. |
| (30) | E-105: protect critical habitat. | Yes. The City’s plans to upgrade facilities, and address possible I/I problems, should reduce discharges and ensure that water quality of the Puget Sound is protected. |
| (31) | E-434: management and protection of water resources by King County through incentives, regulations and programs. | Not applicable. |
| (32) | E-466: protect groundwater and develop strategies to compensate or mitigate for losses. | See above discussion regarding I/I and sewer service to currently unsewered properties. |
| (33) | E-477: protect and enhance surface waters, including Puget Sound. | See above. |
| (34) | F-105: work with cities and service providers to provide services. | Yes. |
| (35) | F-202: ensure adequate supply of public facilities to support communities. | Yes. The City included review and incorporation of information from the most recent comprehensive plan. |
| (36) | F-203: work with cities, special purpose utilities, and other service providers to define regional and local services and determine appropriate providers. | Yes. The City has written agreements with local governments and special purpose utilities regarding service provisions. |
| (37) | F-207: funding for growth should support facilities needed within UGAs, prioritized and coordinated through capital improvement programs, (CIP) to comply with concurrency requirements. | Funding sources are identified to support identified needs, including facilities to serve anticipated population growth under local comprehensive plans. |
| (38) | F-208: support rural levels of development and not facilitate urbanization. | There are no rural areas within the City. |
| (39) | F-210: coordinate development of utility facilities. | Yes. |
| (40) | F-212: King County’s CIP demonstrates that projected needs for facilities and services can be met within the UGA in compliance with concurrency requirements; where not possible, identify strategies including phasing and financing. | Yes. The City’s CIP identifies facilities and a funding strategy, to ensure that it will meet anticipated demands. |
| (41) | F-213: water and sewer utilities that provide services to unincorporated King County shall prepare capital facility plans consistent with requirements of GMA and King County Comprehensive Plan. | Yes. |
| (42) | F-215: King County to initiate sub-area planning process where any service provider declares, in its CIP, an inability to accommodate projected service needs within their service area. | Not applicable. |
| (43) | F-217: where an area wide sewer, water, or transportation deficiency is identified, King County and applicable service providers shall remedy the deficiency through a joint planning process. | Not applicable. |

| (44) | F-245: all development within UGA to be served by public sewers, with some exceptions. | Yes. |
| --- | --- | --- |
| (45) | F-246: King County and sewer utilities should jointly plan for phasing out of on-site systems within UGA. | The City anticipates its service area being almost completely served by sewers. |
| (46) | F-249: public sewers may only be extended into rural and natural resource areas under limited conditions, only if they are tightlined, and only after specific findings are made; utilities shall have written agreements to ensure this; permitted public sewers shall not be allowed to convert rural or natural resource lands to urban uses and densities or to expand permitted nonresidential uses. | Yes, see number 2. |
| (47) | F-250: facilities, such as pump stations, force mains, and trunk lines, which do not serve rural areas, may only be located in rural areas if they are identified in County-approved plans, and with a finding that such facilities are necessary to serve UGA. | Yes, the City’s facilities are consistent with the policy. |
| (48) | F-251: on-site facilities in rural and natural resource areas shall be designed, constructed, and operated as permanent facilities. | Not applicable. No rural or natural resource areas within the City. |
| (49) | F-252: King County should monitor failing on-site systems and analyze options which may include connecting to sewerage systems where consistent with the King County Comprehensive Plan. | No significant number of failing on-site systems within the City’s service area of unincorporated King County. |
| (50) | F-253: collective on-site systems may only be used in rural and natural resource areas under specified conditions. | Not applicable. No rural or natural resource areas within the City. |